## disconnect
Step | IEC 61850 | Description | M/O/C | Function Codes | Data Type
1 | DCND.WinTms | Set Time Window | O | Direct Operate / Response | AI, AO
2 | DCND.RmpTms | Set Ramp Time | O | Direct Operate / Response | AI, AO
3 | DCND.RvrtTms | Set Timeout Period | O | Direct Operate / Response | AI, AO
4 | If switch, CSWI.Pos | Issue switch open control command, and receive response | C | Operate / Response | BI, BO
5 | If not switch, DCND.DERStop | Set ESS to cease to energize and receive confirmation | C | Operate / Response | BI, BO

## reconnect
Step | IEC 61850 | Description | M/O/C | Function Codes | Data Type
1 | DCND.StrWinTms | Set Start Time Window | O | Direct Operate / Response | AI, AO
2 | DCND.RmpTms | Set Ramp Time | O | Direct Operate / Response | AI, AO
3 | DCND.ECPStrAuth | Permission to reconnect | O | Direct Operate / Response | BI, BO
4 | If switch, CSWI.Pos | Issue switch close control command, and receive response | C | Operate / Response | BI, BO
5 | If not switch, DCND.DERStr | Set the ESS to return to service and receive confirmation | C | Operate / Response | BI, BO

## cease_to_energize
Step | IEC 61850 | Description | M/O/C | Function Codes | Data Type
1 | DCTE.WinTms | Set Time Window | O | Direct Operate / Response | AI, AO
2 | DCTE.RmpTms | Set Ramp Time | O | Direct Operate / Response | AI, AO
3 | DCTE.RvrtTms | Set Timeout Period | O | Direct Operate / Response | AI, AO
4 | DCTE.DERStop | Set ESS to cease to energize and receive confirmation | C | Operate / Response | BI, BO

## return_to_service
Step | IEC 61850 | Description | M/O/C | Function Codes | Data Type
1 | DCTE.StrWinTms | Set Start Time Window | O | Direct Operate / Response | AI, AO
2 | DCTE.RmpTms | Set Ramp Time | O | Direct Operate / Response | AI, AO
3 | DCTE.ECPClsAuth | Permission to return to service | O | Direct Operate / Response | BI, BO
4 | DCTE.DERStr | Set the ESS to return to service and receive confirmation | C | Operate / Response | BI, BO

## low_high_voltage_ride_through
Step | IEC 61850 | Description | M/O/C | Function Codes | DNP3 Type
28 | DVRT.ECPRefId | Low/High Voltage Ride-Through Signal Meter ID. Ride through limited voltage spikes and sags, while still ensuring anti-islanding cease-to-energize when required | M |  | AI, AO
29 | DVRT.VolRef | H/LVRT Reference Input. Voltage measurements from the referenced connection point | M |  | AI, AO
30 | DRCT.VRef | Set the Reference Voltage if it is not already set | O | Direct Operate / Response | AI, AO
31 | DRCT.VRegOfs | Set the Reference Voltage Offset if it is not already set | O | Direct Operate / Response | AI, AO
32 | DVRT.CurveVHiTr | Paired array of independent and dependent variables: xVal = time, yVal = HVRT Must Trip voltage values | M | Direct Operate / Response | AI, AO
33 | DVRT.CurveVHiCea | Paired array of independent and dependent variables: xVal = time, yVal = HVRT Momentary Cessation voltage values | O | Direct Operate / Response | AI, AO
34 | DVRT.CurveVLoCea | Paired array of independent and dependent variables: xVal = time, yVal = LVRT Momentary Cessation voltage values | O | Direct Operate / Response | AI, AO
35 | DVRT.CurveVLoTr | Paired array of independent and dependent variables: xVal = time, yVal = LVRT Must Trip voltage values | M | Direct Operate / Response | AI, AO
36 | DVRT.ModEna | Enable Low/High voltage ride- through | M | Select / Response, Operate / Response | BI, BO
37 | DVRT.ModVRtSt | Alarm indicating that a Voltage Ride-Through event has occurred | O |  | BI

## low_high_freq_ride_through
Step | IEC 61850 | Description | M/O/C | Function Codes | DNP3 Type
1 | DFRT.ECPRef | Low/High Frequency Ride-Through Signal Meter ID. Ride through limited voltage spikes and sags, while still ensuring anti-islanding cease-to- energize when required | M |  | AI, AO
2 | DFRT.HzRef | H/LFRT Reference Input. Frequency measurements from the referenced connection point | M |  | AI, AO
3 | DFRT.NomHz | Set the nominal frequency if it is not already set | O | Direct Operate / Response | AI, AO
4 | DFRT.CurveHzHiTr | Paired array of independent and dependent variables: xVal = time, yVal = HFRT Must Trip frequency values | M |  | AI, AO
5 | DFRT.CurveHzHiCea | Paired array of independent and dependent variables: xVal = time, yVal = HFRT Momentary Cessation frequency values | O |  | AI, AO
6 | DFRT.CurveHzLoCea | Paired array of independent and dependent variables: xVal = time, yVal = LFRT Momentary Cessation frequency values | O |  | AI, AO
7 | DFRT.CurveHzLoTr | Paired array of independent and dependent variables: xVal = time, yVal = LFRT Must Trip frequency values | M |  | AI, AO
8 | DFRT.ModEna | Enable Low/High voltage ride-through | M | Select / Response, Operate / Response | BI, BO
9 | DFRT.ModHzRtSt | Alarm indicating that a Frequency Ride-Through event has occurred | O |  | BI

## dynamic_reactive_current
Step | IEC 61850 | Description | M/O/C | Function Codes | Data Type
1 | RDGS.ECPRefId | Referenced ECP | O |  | AI, AO
2 | RDGS.ArGraMod | Mode of reactive current characteristic: selects between that behaviour where gradients trend toward zero at the deadband edges, and where the gradients trend toward zero at the centre. False = Gradients trend toward zero at the deadband. True = Gradient trend toward zero at the center. | O |  | AI, AO
3 | RDGS.DbVMin | This is a voltage deviation relative to Vaverage, expressed in terms of % of Vref (for example -10%Vref). For negative voltage deviations (voltage below the moving average) that are smaller in amplitude than this amount, no additional dynamic reactive current is produced. | O |  | AI, AO
4 | RDGS.DbVMax | This is a voltage deviation relative to Vaverage, expressed in terms of % of Vref (for example +10%Vref). For positive voltage deviations (voltage above the moving average) that are smaller in amplitude than this amount, no additional dynamic reactive current is produced. Together, DbVMin and DbVMax allow for the creation of a deadband, inside of which the system does not generate additional reactive current support. | O |  | AI, AO
5 | RDGS.ArGraSag | This is a gradient, expressed in unit-less terms of %/%, to establish the ratio by which Capacitive % VAr production is increased as %Delta-Voltage decreases below DbVMin. Note that the % Delta- Voltage may be calculated relative to Moving Average of Voltage + DbVMin (as shown in Figure 16-1) or relative to Moving Average of Voltage (as shown in Figure 16-4), according to the ArGraMod setting. | O |  | AI, AO
6 | RDGS.ArGraSwl | This is a gradient, expressed in unit- less terms of %/%, to establish the ratio by which Inductive % VAr production is increased as %Delta- Voltage increases above DbVMax. Note that the % Delta-Voltage may be calculated relative to Moving Average of Voltage. DbVMax (as shown in Figure 16-1) or relative to Moving Average of Voltage (as shown in Figure 16-4), according to the ArGraMod setting. | O |  | AI, AO
7 | RDGS.FilTms | This is the time, expressed in seconds, over which the moving linear average of voltage is calculated to determine the Delta-Voltage. | O |  | AI, AO
8 | RDGS.HysBlkZnV | Hysteresis voltage | O |  | AI, AO
9 | RDGS.BlkZnV | Block zone voltage | O |  | AI, AO
10 | RDGS.BlkZnTmms | Block zone time (in milliseconds) | O |  | AI, AO
11 | RDGS.HoldTmms | Hold time (in milliseconds) | O |  | AI, AO
12 | RDGS.ModPrity | Dynamic Reactive Current Support Mode Priority | O |  | AI, AO
13 | RDGS.ModEna | Enable/disable dynamic reactive current support mode | M |  | BI
14 | RDGS.EvtEna (not in IEC 61850 yet) | This is a Boolean that selects whether or not the event-based behavior is enabled. | O |  | BI, BO
15 | RDGS.VArMaxAvl (not in IEC 61850 yet) | This is a Boolean that selects the priority of whether or not Watts should be curtailed in order to produce the reactive current required by this function. | O |  | BI, BO
16 | RDGS.DelV | Delta voltage measurement | O |  | AI
17 | RDGS.VAv | Moving average voltage calculation | O |  | AI

## dynamic_volt_watt
Step | IEC 61850 | Description | M/O/C | Function Codes | Data Type
1 | DVWD.ECPRefId | Referenced ECP | M |  | AI, AO
2 | DVWD.DynVWGra | Dynamic Volt-Watt Gradient. Signed unit-less quantity that establishes the ratio of additional Watts supplied (expressed in terms of % DRCT.WMax) to the present difference from the moving average voltage (expressed as % DRCT.VRef). | M |  | AI, AO
3 | DVWD.VWFilTms | Dynamic Volt-Watt Filter Time. The time in seconds used to calculate the moving average voltage for dynamic Volt-Watt support. | O |  | AI, AO
4 | DVWD.DbVWLo | Dynamic Volt-Watt Lower Deadband. Percentage of the nominal voltage (DRCT.Vref) measured below the moving average voltage. If the present voltage is above this value, no additional Watts shall be supplied. | O |  | AI, AO
5 | DVWD.DbVWHi | Dynamic Volt-Watt Upper Deadband. Percentage of the nominal voltage (DRCT.Vref) measured above the moving average voltage. If the present voltage is below this value, no additional Watts shall be supplied. | O |  | AI, AO
6 | DVWD.RevtTms | Dynamic Volt-Watt Reversion Timeout Period | O |  | AI, AO
7 | DVWD.ModEna | Enable/disable dynamic Volt-Watt mode | O |  | AI, AO
8 | DVWD.ModPrty | Dynamic Volt-Watt Mode Priority | O |  | AI, AO
9 | DVWD.DelV | Delta voltage measurement | O |  | AI
10 | DVWD.VAv | Moving average voltage calculation | O |  | AI

## frequency_watt_emergency
Step | IEC 61850 | Description | M/O/C | Function Codes | Data Type
1 | FWHZ.ECPRefId | Set Referenced ECP | M |  | AI, AO
2 | FWHZ.HzRef | Frequency measurement from the Referenced ECP | M |  | AI
3 | FWHZ.WinTms | Time window within which to randomly initiate mode | O | Direct Operate / Response | AI, AO
4 | FWHZ.RmpTms | Ramp time for moving from current operational mode settings to new operational mode settings | O | Direct Operate / Response | AI, AO
5 | FWHZ.RvrtTms | Reversion timeout period upon which to take reversion default action | O | Direct Operate / Response | AI, AO
6 | DOPR.ECPNomHz | Nominal frequency | M |  | AI, AO
7 | FWHZ.HzStr | F-W Starting frequency: Delta frequency between start frequency and nominal grid frequency | M | Direct Operate / Response | AI, AO
8 | FWHZ.HzStop | F-W Stopping frequency: Delta frequency between stop frequency and nominal grid frequency | M | Direct Operate / Response | AI, AO
9 | FWHZ.HzStopWGra | F-W Maximum W change rate: The maximum rate at which the output may be increased after releasing the frozen value of snap shot function. This is represented in terms of % WMax per minute. | O | Direct Operate / Response | AI, AO
10 | FWHZ.ActDlTmms | F-W Activation delay: Intentional delay in ms before function activation | O | Direct Operate / Response | AI, AO
11 | FWHZ.HysEna | F-W Hysteresis enable/disable True = Use of hysteresis; False = No use of hysteresis | O | Direct Operate / Response | AI, AO
12 | FWHZ.SnptW | F-W Snapshot of power: True = Snapshot is active; False = Off, the snapshot is not active | O | Direct Operate / Response | AI, AO
13 | FWHZ.ModPrty | Freq-Watt Emergency Mode Priority | O | Direct Operate / Response | AI, AO
14 | FWHZ.WCtlHzEna | F-W enable | M |  | BI, BO

## charge_discharge
Step | IEC 61850 | Description | M/O/C | Function Codes | Data Type
1 | DCHD.WinTms | Time window within which to randomly initiate mode | O | Direct Operate / Response | AI, AO
2 | DCHD.RmpTms | Ramp time for moving from current operational mode settings to new operational mode settings | O |  | AI, AO
3 | DCHD.RvrtTms | Reversion timeout period upon which to take reversion default action | O | Direct Operate / Response | AI, AO
4 | DCHD.WTgt | Set charge or discharge target. Positive is discharging, negative is charging | M | Direct Operate / Response | AI, AO
5 | DCHD.RmpUpRte | Discharging ramp up rate | O | Direct Operate / Response | AI, AO
6 | DCHD.RmpDnRte | Discharging ramp down rate | O | Direct Operate / Response | AI, AO
7 | DCHD.ChaRmpUpRte | Charging ramp up rate | O |  | AI, AO
8 | DCHD.ChaRmpDnRte | Charging ramp down rate | O |  | AI, AO
9 | DCHD.ModPrty | Charge/Discharge Mode Priority | O |  | AI, AO
10 | DCHD.VArAct | Charge/Discharge VAr Action to take when switching between charging and discharging: <0> Reserved, <1> Reverse: producing/absorbing Vars when changing between charging and discharging (go to diagonal quadrant Q1/Q3 or Q2/Q4), <2> Do not reverse: producing/absorbing Vars (go to adjacent quadrant Q1/Q2 or Q3/Q4) | O |  | AI, AO
11 | DCHD.ModEna | Enable Charge/Discharge mode and receive response | M | Select / Response, Operate / Response | BI, BO

## coordinated_charge_discharge
Step | IEC 61850 | Description | M/O/C | Function Codes | Data Type
12 | DTCD.WinTms | Time window within which to randomly initiate mode. | O | Direct Operate / Response | AI, AO
13 | DTCD.RmpTms | Ramp time for moving from current operational mode settings to new operational mode settings. | O | Direct Operate / Response | AI, AO
14 | DTCD.RvrtTms | Reversion timeout period upon which to take reversion default action. | O | Direct Operate / Response | AI, AO
15 | DTCD.SOCUseTgt | Target usable state of charge that the system is expected to achieve, as a percentage of the usable capacity. | M |  | AI, AO
16 | DTCD.DateTgt | Target date and time by which the storage system must reach the target SOC. | C |  | AI, AO
17 | DTCD.Tms.Tgt | Target duration to move from the current SOC to the target SOC. | C |  | AI, AO
18 | DTCD.ModEna | Coordinated Charge/Discharge mode enable. | M |  | BI,BO
19 | DRCT.MaxRmpUpRte | Maximum Ramp Up Rate. Ramp up rate during generating (discharging). Ramp rate as percentage of NomRmpUpRte. | O |  | AI
20 | DRCT.MaxRmpDnRte | Maximum Ramp Down Rate. As percentage of nominal maximum ramp rate. Ramp down rate during generating (discharging). Ramp rate as percentage of NomRmpDnRte. | O |  | AI

## active_power_limit
Step | IEC 61850 | Description | M/O/C | Function Codes | Data Type
1 | DAMG.ECPRefId | Set Referenced ECP | M |  | AI, AO
2 | DAMG.WRef | Measurement from the Referenced ECP | M |  | AI
3 | DAMG.WinTms | Time window within which to randomly initiate mode | O | Direct Operate / Response | AI, AO
4 | DAMG.RmpTms | Ramp time for moving from current operational mode settings to new operational mode settings | O | Direct Operate / Response | AI, AO
5 | DAMG.RvrtTms | Reversion timeout period upon which to take reversion default action | O | Direct Operate / Response | AI, AO
6 | DAMG.WImpLimPct | Active Power Limit Charge Setpoint. Limit of imported Watts as a percentage of Maximum Active Power capability | C |  | AI, AO
7 | DAMG.WExpLimPct | Active Power Limit Discharge Setpoint. Limit of exported Watts as a percentage of Maximum Active Power capability | C |  | AI, AO
8 | DAMG.ModPrty | Active Power Limit Mode Priority | O |  | AI, AO
9 | DAMG.ModEna | Enable Limited Watts mode and receive response | M | Select / Response, Operate / Response

## peak_power_limiting
Step | IEC 61850 | Description | M/O/C | Function Codes | Data Type
1 | DPKP.ECPRefId | Referenced ECP | M |  | AI, AO
2 | DPKP.WRef | Measurement from the Referenced ECP | M |  | AI
3 | DPKP.WinTms | Time window within which to randomly initiate mode | O | Direct Operate / Response | AI, AO
4 | DPKP.RmpTms | Ramp time for moving from current operational mode settings to new operational mode settings | O | Direct Operate / Response | AI, AO
5 | DPKP.RvrtTms | Reversion timeout period upon which to take reversion default action | O | Direct Operate / Response | AI, AO
6 | DPKP.PkPwrWLim | Target value of the reference load power in watts. The ESS shall generate watts to ensure the reference load does not exceed this limit. | C |  | AI, AO
7 | DPKP.PkPwrFolPct | Peak Power Limiting Ratio. If 100%, then peak power is limited to the limit value. If < 100%, then peak power is limited to the remaining percentage over the limit. | C |  | AI, AO
8 | DPKP.RmpUpRte | Discharging Ramp Up Rate. Maximum ramp up rate | O |  | AI, AO
9 | DPKP.RmpDnRte | Discharging Ramp Down Rate. Maximum ramp down rate | O |  | AI, AO
10 | DPKP.ModPrty | Active Power Limit Mode Priority | O |  | AI, AO
11 | DPKP.ModEna | Enable Limited Watts mode and receive response | M | Select / Response, Operate / Response

## load_following
Step | IEC 61850 | Description | M/O/C | Function Codes | Data Type
1 | DLFL.ECPRefId | Set the Referenced ECP | M |  | AI, AO
2 | DLFL.WRef | Measurement from the Referenced ECP | M |  | AI
3 | DLFL.WinTms | Time window within which to randomly initiate mode | O | Direct Operate / Response | AI, AO
4 | DLFL.RmpTms | Ramp time for moving from current operational mode settings to new operational mode settings | O | Direct Operate / Response | AI, AO
5 | DLFL.RvrtTms | Reversion timeout period upon which to take reversion default action | O | Direct Operate / Response | AI, AO
6 | DLFL.LodFolThrshW | Threshold to start actively following load in watts. | M |  | AI, AO
7 | DLFL.PkPwrFolPct | Load Following Ratio. If 100%, then Load Following follows the load exactly. If < 100%, then Load Following follows the load as a percentage of the load over the threshold. | O |  | AI, AO
8 | DLFL.RmpUpRte | Discharging Ramp Up Rate. Maximum ramp up rate | O |  | AI, AO
9 | DLFL.RmpDnRte | Discharging Ramp Down Rate. Maximum ramp down rate | O |  | AI, AO
10 | DLFL.ModPrty | Active Power Limit Mode Priority | O |  | AI, AO
11 | DLFL.ModEna | Enable Limited Watts mode and receive response | M | Select / Response, Operate / Response | BI

## generation_following
Step | IEC 61850 | Description | M/O/C | Function Codes | Data Type
1 | DGFL.ECPRefId | Set the Referenced ECP | M |  | AI, AO
2 | DGFL.WRef | Measurement from the Referenced ECP | M |  | AI
3 | DGFL.WinTms | Time window within which to randomly initiate mode | O | Direct Operate / Response | AI, AO
4 | DGFL.RmpTms | Ramp time for moving from current operational mode settings to new operational mode settings | O | Direct Operate / Response | AI, AO
5 | DGFL.RvrtTms | Reversion timeout period upon which to take reversion default action | O | Direct Operate / Response | AI, AO
6 | DGFL.GenFolThrshW | Threshold to start actively following generation in watts. | M |  | AI, AO
7 | DGFL.GenFolPct | Generation Following Ratio. If 100%, then Load Following follows the load exactly. If < 100%, then Load Following follows the load as a percentage of the load over the threshold. | O |  | AI, AO
8 | DGFL.RmpUpRte | Discharging Ramp Up Rate. Maximum ramp up rate | O |  | AI, AO
9 | DGFL.RmpDnRte | Discharging Ramp Down Rate. Maximum ramp down rate | O |  | AI, AO
10 | DGFL.ChaRmpUpRte | Charging ramp up rate Maximum ramp up rate | O |  | AI, AO
11 | DGFL.ChaRmpDnRte | Charging ramp down rate Maximum ramp up rate | O |  | AI, AO
12 | DGFL.ModPrty | Active Power Limit Mode Priority | O |  | AI, AO
13 | DGFL.ModEna | Enable Limited Watts mode and receive response | M | Select / Response, Operate / Response | BI

## automatic_generation_control
Step | IEC 61850 | Description | M/O/C | Function Codes | Data Type
1 | DAGC.WinTms | Time window within which to randomly initiate mode | O | Direct Operate / Response | AI, AO
2 | DAGC.RmpTms | Ramp time for moving from current operational mode settings to new operational mode settings | O | Direct Operate / Response | AI, AO
3 | DAGC.RvrtTms | Reversion timeout period upon which to take reversion default action | O | Direct Operate / Response | AI, AO
4 | DAGC.RmpUpTms | Set ramp up time by which the Active Power target is reached | O | Direct Operate / Response | AI, AO
5 | DAGC.RmpDnTms | Set ramp down time by which the Active Power target is reached | O | Direct Operate / Response | AI, AO
6 | DAGC.SOCUseMin | Minimum Usable SOC for AGC | O |  | AI, AO
7 | DAGC.SOCUseMax | Maximum Usable SOC for AGC | O |  | AI, AO
8 | DAGC.PerTms | Periodicity of AGC signals | O | Direct Operate / Response | AI, AO
9 | DAGC.WTgt | Set charge or discharge Active Power target in watts. Positive is discharging, negative is charging | M | Direct Operate / Response | AI, AO
10 | DAGC.ModEna | Enable Charge/Discharge mode and receive response | M | Select / Response, Operate / Response | BI, BO
11 | DAGC.ModPrty | AGC Mode Priority | O |  | AI, AO
12 | DRCT.MaxRmpUpRte | Maximum Ramp Up Rate. Ramp up rate during generating (discharging). Ramp rate as percentage of NomRmpUpRte. | O |  | AI
13 | DRCT.MaxRmpDnRte | Maximum Ramp Down Rate. As percentage of nominal maximum ramp rate. Ramp down rate during generating (discharging). Ramp rate as percentage of NomRmpDnRte. | O |  | AI

## active_power_smoothing
Step | IEC 61850 | Description | M/O/C | Function Codes | Data Type
1 | DWSM.ECPRefId | Set the Referenced ECP | M |  | AI, AO
2 | DWSM.WRef | Measurement from the Referenced ECP | M |  | AI
3 | DWSM.WinTms | Time window within which to randomly initiate mode | O | Direct Operate / Response | AI, AO
4 | DWSM.RmpTms | Ramp time for moving from current operational mode settings to new operational mode settings | O | Direct Operate / Response | AI, AO
5 | DWSM.RvrtTms | Reversion timeout period upon which to take reversion default action | O | Direct Operate / Response | AI, AO
6 | DWSM.WSmthGra | Active Power Smoothing Gradient. Signed quantity that establishes the ratio of additional smoothing Watts provided to the present Delta Watts of the reference load or generation. Delta Watts is the difference between the moving average and the present value of the reference power. | M |  | AI, AO
7 | DWSM.WSmthLoLim | Active Power Smoothing Lower Limit. Difference in Watts from the moving average of the reference power above which no smoothing shall be applied. | O |  | AI, AO
8 | DWSM.WSmthHiLim | Active Power Smoothing Upper Limit. Difference in Watts from the moving average of the reference power below which no smoothing shall be applied. | O |  | AI, AO
9 | DWSM.FilTms | Active Power Smoothing Filter Time (seconds). Time used to calculate the moving average of the reference load or generation being smoothed. | O |  | AI, AO
10 | DWSM.RmpUpRte | Discharging Ramp Up Rate. Maximum ramp up rate | O |  | AI, AO
11 | DWSM.RmpDnRte | Discharging Ramp Down Rate. Maximum ramp down rate | O |  | AI, AO
12 | DWSM.ChaRmpUpRte | Charge Ramp Up Rate. Maximum ramp up rate | O |  | AI, AO
13 | DWSM.ChaRmpDnRte | Charge Ramp Down Rate. Maximum ramp up rate | O |  | AI, AO
14 | DWSM.ModPrty | Active Power Limit Mode Priority | O |  | AI, AO
15 | DWSM.ModEna | Enable Limited Watts mode and receive response | M | Select / Response, Operate / Response | BI

## volt_watt
Step | IEC 61850 | Description | M/O/C | Function Codes | Data Type
1 | DVWG.ECPRefId | Set the Referenced ECP | M |  | AI, AO
2 | DVWG.WRef | Measurement from the Referenced ECP | M |  | AI
3 | DVWG.WinTms | Time window within which to randomly initiate mode | O | Direct Operate / Response | AI, AO
4 | DVWG.RmpTms | Ramp time for moving from current operational mode settings to new operational mode settings | O | Direct Operate / Response | AI, AO
5 | DVWG.RvrtTms | Reversion timeout period upon which to take reversion default action | O | Direct Operate / Response | AI, AO
6 | DVWG.VWDecGra | Volt-Watt Decreasing Watt Gradient. Percent of WMax | M |  | AI, AO
7 | DVWG.VWIncrGra | Volt-Watt Increasing Watt Gradient. Percent of WMax or AMax (depending on Watts/Amps agreement) | O |  | AI, AO
8 | DVWG.VWLoLim | Volt-Watt Lower Limit: start to increase export of watts | O |  | AI, AO
9 | DVWG.VWHiLim | Volt-Watt Upper Limit: start to decrease export of watts | O |  | AI, AO
10 | DVWG.FilTms | Volt-Watt Filter Time (Seconds) | O |  | AI, AO
11 | DVWG.RmpUpRte | Volt-Watt Discharging Ramp Up Rate. Maximum ramp up rate | O |  | AI, AO
12 | DVWG.RmpDnRte | Volt-Watt Discharging Ramp Down Rate. Maximum ramp down rate | O |  | AI, AO
13 | DVWG.ChaRmpUpRte | Volt-Watt Charge Ramp Up Rate. Maximum charging ramp up rate | O |  | AI, AO
14 | DVWG.ChaRmpDnRte | Volt-Watt Charge Ramp Down Rate. Maximum charging ramp down rate | O |  | AI, AO
15 | DVWG.ModPrty | Active Power Limit Mode Priority | O |  | AI, AO
16 | DVWG.ModEna | Enable Limited Watts mode and receive response | M | Select / Response, Operate / Response | BI

## frequency_watt_curve
Step | IEC 61850 | Description | M/O/C | Function Codes | Data Type
1 | DFWS.ECPRefId | Set Referenced ECP | M |  | AI, AO
2 | DFWS.HzRef | Frequency measurement from the Referenced ECP | M |  | AI
3 | DOPR.ECPNomHz | Nominal frequency | O |  | AI, AO
4 | DFWS.PairArrHzW | Curve of Frequency-Watt pairs | M |  | AI, AO
5 | DFWS.WinTms | Time window within which to randomly initiate mode | O | Direct Operate / Response | AI, AO
6 | DFWS.RmpTms | Ramp time for moving from current operational mode settings to new operational mode settings | O | Direct Operate / Response | AI, AO
7 | DFWS.RvrtTms | Reversion timeout period upon which to take reversion default action | O | Direct Operate / Response | AI, AO
8 | DFWS.Mod | F-W enable | M |  | BI, BO

## fixed_power_factor
Step | IEC 61850 | Description | M/O/C | Function Codes | Data Type
1 | DFPF.ECPRefId | Set Referenced ECP | M |  | AI, AO
2 | DFPF.PFRef | PF measurement from the Referenced ECP | M |  | AI
3 | DFPF.WinTms | Time window within which to randomly initiate mode | O | Direct Operate / Response | AI, AO
4 | DFPF.RmpTms | Ramp time for moving from current operational mode settings to new operational mode settings | O | Direct Operate / Response | AI, AO
5 | DFPF.RvrtTms | Reversion timeout period upon which to take reversion default action | O | Direct Operate / Response | AI, AO
6 | DFPF.PFTgt | Target Power Factor | M |  | AI, AO
7 | DFPF.ModEna | Enable fixed PF mode | M |  | BI, BO
8 | DFPF.ModPrty | Fixed Power Factor Mode Priority | O |  | AI, AO

## volt_var_control
Step | IEC 61850 | Description | M/O/C | Function Codes | Data Type
1 | DVVC.ECPRefId | Set Referenced ECP | M |  | AI, AO
2 | DVVC.VRef | Voltage measurement from the Referenced ECP | M |  | AI
3 | DVVC.WinTms | Time window within which to randomly initiate mode | O | Direct Operate / Response | AI, AO
4 | DVVC.RmpTms | Ramp time for moving from current operational mode settings to new operational mode settings | O | Direct Operate / Response | AI, AO
5 | DVVC.RvrtTms | Reversion timeout period upon which to take reversion default action | O | Direct Operate / Response | AI, AO
6 | DVVC.PairArrVVar | Volt-VAR curve, using CSG | M |  | AI, AO
7 | DVVC.ModEna | Volt-VAR enable | M |  | BI, BO
8 | DVVC.ModPrty | Volt-VAR Control Mode Priority | O |  | AI, AO

## watt_var
Step | IEC 61850 | Description | M/O /C | Function Codes | Data Type
1 | DWVR.ECPRefId | Set Referenced ECP | M |  | AI, AO
2 | DWVR.VRef | Voltage measurement from the Referenced ECP | M |  | AI
3 | DWVR.WinTms | Time window within which to randomly initiate mode | O | Direct Operate / Response | AI, AO
4 | DWVR.RmpTms | Ramp time for moving from current operational mode settings to new operational mode settings | O | Direct Operate / Response | AI, AO
5 | DWVR.RvrtTms | Reversion timeout period upon which to take reversion default action | O | Direct Operate / Response | AI, AO
6 | DWVR.PairArrVVar | Watt-VAr curve, using CSG | M |  | AI, AO
7 | DWVR.ModEna | Watt-VAr enable | M |  | BI, BO
8 | DWVR.ModPrty | Watt-VAr Control Mode Priority | O |  | AI, AO

## power_factor_limiting
Step | IEC 61850 | Description | M/O/C | Function Codes | Data Type
1 | DPFC.ECPRefId | Set Referenced ECP | M |  | AI, AO
2 | DPFC.PFRef | PF measurement from the Referenced ECP | M |  | AI
3 | DPFC.WinTms | Time window within which to randomly initiate mode | O | Direct Operate / Response | AI, AO
4 | DPFC.RmpTms | Ramp time for moving from current operational mode settings to new operational mode settings | O | Direct Operate / Response | AI, AO
5 | DPFC.RvrtTms | Reversion timeout period upon which to take reversion default action | O | Direct Operate / Response | AI, AO
6 | DPFC.PFRef.rangeC | Power Factor Limiting Lower PF Limit | M |  | AI, AO
7 | DPFC.PFRef.rangeC | Power Factor Limiting Upper PF Limit
8 | DPFC.ModPrty | Power Factor Correction Mode Priority | O |  | AI, AO
9 | DPFC.ModEna | Power Factor Correction enable | M |  | BI, BO

## schedule_creation
Step | IEC 61850 | Description | M/O/C | Function Codes | Data Type
1 | FSCHxx (the xx refers to the schedule number (index) | Select which schedule to edit by writing a number to this point. This is the “index” of the schedule, not its “identity”. The indexes shall be the monotonically increasing integers 1, 2, 3, etc. while the curve identities may be any unique number. | M | Direct Operate / Response | AI, AO
2 | FSCHxx.ValASG (with FSCH.ClcIntvTyp set to seconds) | Set the Time Offset (X-Value) for each schedule point. Time Offsets must increase with each point. Time Offsets represent relative seconds from each repetition of the schedule. | O | Direct Operate / Response | AI, AO
3 | FSCHxx.ValASG (set for power system values and pricing signals) | Set the Y-value for each schedule point for power system values (watts,VARs, PF, pricing signal, etc.). | O | Direct Operate / Response | AI, AO
4 | FSCHxx.ING (set to the operational mode identity) | Set the Y-value for enabling or disabling operational modes (VV, FW, VW, etc.) at each schedule point. | C |  | AI, AO
5 | FSCHxx.RmpTms | Set the Ramp Type for entire schedule point. | O | Direct Operate / Response | AI, AO
6 | FSCHxx.NumEntr | Set the number of points used for the schedule. Set this value to zero to disable the schedule (there are other ways to enable and disable schedules). | M | Direct Operate / Response | AI, AO
7 | FSCHxx.SchdPrio | Set the priority for the schedule. | O | Direct Operate / Response | AI, AO
8 | FSCHxx.ValMV (for power system values or pricing signals) or FSCH.ValINS (for operational modes) (meanings of pricing signals need to be defined) | Set the meaning of the Y-values of the schedule. | O | Direct Operate / Response | AI, AO

## schedule_enable
Step | IEC 61850 | Description | M / O /C | Function Codes | Data Type
1 | FSCC.Schd | Identify the schedule to enable | M | Direct Operate / Response | AI, AO
2 | FSCHxx.StrTm | Set the start time for the selected schedule. TBD: Discuss time format for DNP3. | M | Direct Operate / Response | AI, AO
3 | FSCHxx.IntvPer | Set the repeat interval for the selected schedule | O | Direct Operate /Response | AI, AO
4 | FSCHxx.ClcIntvTyp | Set the repeat interval units for the selected schedule | O | Direct Operate / Response | AI, AO
5 | FSCHxx.Enable | Enable the Schedule by changing its state to “ready” | M | Select / Response, Operate / Response | BI, BO
6 | FSCH.SchdSt.2 | Selected Schedule is Validated | O |  | BI, BO
7 | FSCHxx.SchdReuse | Selected Schedule Repeat Weekly Sunday | O |  | BI, BO
8 | FSCHxx.SchdReuse | Selected Schedule Repeat Weekly Monday | O |  | BI, BO
9 | FSCHxx.SchdReuse | Selected Schedule Repeat Weekly Tuesday | O |  | BI, BO
10 | FSCHxx.SchdReuse | Selected Schedule Repeat Weekly Wednesday | O |  | BI, BO
11 | FSCHxx.SchdReuse | Selected Schedule Repeat Weekly Thursday | O |  | BI, BO
12 | FSCHxx.SchdReuse | Selected Schedule Repeat Weekly Friday | O |  | BI, BO
13 | FSCHxx.SchdReuse | Selected Schedule Repeat Weekly Saturday | O |  | BI, BO
14 | FSCC.ActSchdRef | One of more Schedules Running | O |  | BI, BO

## curve
Step | IEC 61850 | Description | M/O/C | Function Codes | Data Type
1 | Curve Edit Selector | Curve Edit Selector | M
2 | Curve Mode Type | Curve Mode Type
3 | Curve Time Window | Curve Time Window
4 | Curve Ramp Time | Curve Ramp Time
5 | Curve Revert Time | Curve Revert Time
6 | Curve Maximum Number of Points | Curve Maximum Number of Points
7 | Independent (X-Value) Units for Curve | Independent (X-Value) Units for Curve
8 | Dependent (Y-Value) Units for Curve | Dependent (Y-Value) Units for Curve
9 | Curve Time Constant | Curve Time Constant
10 | Curve Decreasing Max Ramp Rate | Curve Decreasing Max Ramp Rate
11 | Curve Increasing Ramp Rate | Curve Increasing Ramp Rate
12 | CurveStart | CurveStart
13 | Curve Number of Points | Curve Number of Points | M