## Key
DNP3 Profile for DER Communications
Draft Points List - November 15, 2016
| Symbol/Function | Meaning
| BI | SCADA and configuration binary input.
| BO | SCADA and configuration binary output.
| C | SCADA and configuration counter.
| AI | SCADA and configuration analog input.
| AO | SCADA and configuration analog output.
| S | Start of scheduling points.
| HM | Start of historical meter points.
| HDU | Start of historical DER unit points.
| HI | Start of historical inverter points.
| HB | Start of historical inverter points.
| mhbi(n) | Starting index of meter #n binary inputs relative to HM.
| duhbi(n) | Starting index of DER unit #n binary inputs relative to HDU.
| ihbi(n) | Starting index of inverter #n binary inputs relative to HI.
| bhbi(n) | Starting index of battery #n binary inputs relative to HB.
| ductr(n) | Starting index of DER Unit #n counters.
| mhai(n) | Starting index of meter #n analog inputs relative to HM.
| duhai(n) | Starting index of DER unit #n analog inputs relative to HDU.
| ihai(n) | Starting index of inverter #n analog inputs relative to HI.
| bhai(n) | Starting index of battery #n analog inputs relative to HB.
| mhai(n) | Starting index of meter #n analog outputs relative to HM.
| ihai(n) | Starting index of inverter #n analog outputs relative to HI.
| bhai(n) | Starting index of battery #n analog outputs relative to HB.

## BI
Temp | Point Index | Name / Description | Default Event Class | Name for State when value is 0 | Name for State when value is 1 | LN Class | LN Inst | Data Object | CDC | Function | Unique String | MESA-ESS | Note1 | Note2
| #REF! | System Communication Error |  | Normal | Alarm: Communications error exists in the ESS | LCCH |  | ChLiv | SPS |  | LCCH.ChLiv | Yes | New, from MESA alarm set
| BI0 | System Has P1 Alarms |  | No P1 Alarms Active | Alarm: One or More P1 Alarms Active | CALH |  | GrAlm | SPS |  | CALH.GrAlm | Yes | New, from MESA alarm set | Which alarms to include is not explicitly established - this object just acts as the OR'ing of other alarms
| #REF! | System Has P2 Alarms |  | No P2 Alarms Active | Alarm: One or More P2 Alarms Active | CALH |  | GrAlm | SPS |  | CALH.GrAlm | Yes | New, from MESA alarm set
| #REF! | System Has P3 Alarms |  | No P3 Alarms Active | Alarm: One or More P3 Alarms Active | CALH |  | GrAlm | SPS |  | CALH.GrAlm | Yes | New, from MESA alarm set
| BI1 | Storage state of charge (percent) is too high | 1 | Normal | Alarm | DBAT |  | BatHi | SPS |  | DBAT.BatHi | Yes | New | Should we add BatHiRsv?
| BI2 | Storage state of charge is too low - reserve reached | 1 | Normal | Alarm | DBAT |  | BatLoRsv | SPS |  | DBAT.BatLoRsv | Yes | New | DCTE
| BI3 | Storage state of charge is depleted - minimum rating reached | 1 | Normal | Alarm | DBAT |  | BatLo | SPS |  | DBAT.BatLo | Yes | New | DCTE
| BI4 | Storage internal temperature too high | 1 | Normal | Alarm | DBAT |  | IntnBatTmp.range | MV |  | DBAT.IntnBatTmp.range | Yes | New
| BI5 | Storage external (ambient) temperature too high | 1 | Normal | Alarm | MMET |  | EnvTmp.range | MV |  | MMET.EnvTmp.range | Yes | New | In 7-4
| BI6 | System Is In Lockout State. System has been locked by an operator such that other operators may not execute commands. | 2 | System locked out | System lnot locked out | DRCS |  | ModLkd | SPS |  | DRCS.ModLkd | Yes | New, added per item 31 | Note: If system is not in either local or lockout state, then it is in remote.
| BI7 | System Is In Local State. System has been locked by a local operator which prevents other operators from executing commands. Note: Local State is also sometimes referred to ask Maintenance State. | 2 | System in local state | System not in local state | DRCS |  | ModTest | SPC |  | DRCS.ModTest | Yes | New, added per item 31 | "Local" term used rather than "maintenance".
| BI8 | System is in automatic mode | 3 | Not-Auto | Auto | DRCS |  | AutoMan | SPS |  | DRCS.AutoMan | Yes | Per item #36 | Included because mandatory. MESA will not implement,
| BI9 | System Is Starting Up. Set to 1 when a BO "System Initiate Start-up Sequence" command has been received. |  | Not Starting Up | Start command has been received. | DRCS |  | ModStr | SPS |  | DRCS.ModStr | Yes | New, added per item 31
| BI10 | System Is Stopping Set to 1 when an B0 "System Execute Stop" command has been received. |  | Not Stopping | Emergency stop command (BO 02) has not been received. | DRCS |  | ModStop |  |  | DRCS.ModStop | Yes | New | Added as corresponding BI
| BI11 | System is Started (Return to Service). If any of the inverters is started, then true. | 2 | Null | Started | DRCC |  | DERStr | SPC |  | DRCC.DERStr | Yes | Description made general
| BI12 | System is Stopped (Cease to Energize). If all of the inverters are stopped, then true. | 2 | Null | Stopped | DCTE |  | DERStop | SPC |  | DCTE.DERStop | Yes | Description made general
| BI13 | System Permission to Start Status |  | Start Permission Not Granted | Start Permission Granted | DOPA |  | DERStrAuth | SPC |  | DOPA.DERStrAuth | Yes | New | Added as corresponding BI
| BI14 | System Permission to Stop Status |  | Stop Permission Not Granted | Stop Permission Granted | DOPA |  | ECPOpnAuth | SPC |  | DOPA.ECPOpnAuth | Yes | New | Added as corresponding BI
| BI15 | DER is generating and connected | 3 | Null | On-Connected | DRCS |  | ModOnConn | SPS |  | DRCS.ModOnConn | Yes | Per item #36 | Instead of ZINV.GridModSt
| BI16 | DER is generating and available for connection | 3 | Null | On-Not-Connected | DRCS |  | ModOnAvl | SPS |  | DRCS.ModOnAvl | Yes | Per item #36 | Instead of ZINV.GridModSt
| BI20 | DER is generating and not available for connection | 3 | Null |  | DRCS |  | ModOnUnavl |  |  | DRCS.ModOnUnavl | Yes |  | On, not connected, and not available to connect
| BI17 | DER is off but available to start | 3 | Null | Off-Available | DRCS |  | ModOffAvl | SPS |  | DRCS.ModOffAvl | Yes | Per item #36 | Instead of ZINV.GridModSt
| BI18 | DER is off and not available to start | 3 | Null | Off-Not-Available | DRCS |  | ModOffUnavl | SPS |  | DRCS.ModOffUnavl | Yes | Per item #36 | Instead of ZINV.GridModSt
| BI19 | DER is charging and connected | 3 | Null |  | DRCS |  | ModConnCha | SPS |  | DRCS.ModConnCha | Yes
| BI22 | DER connect/ disconnect switch open/close status | 2 | Open | Closed | CSWI |  | Pos | DPC | INV1 | CSWI. Pos | Yes | Keep
| BI23 | DER connect/ disconnect switch movement status | 2 | Not Moving | Moving | CSWI |  | Pos | DPC | INV1 | CSWI. Pos | Yes | Keep, added second BI as DNP3 level 2 does not support double bit binaries
| BI24 | Islanded Mode. Determines how the DER behaves when in an Islanded configuration. <0> Isochronous Mode. DER attempts to control voltage and frequency independent of configured curves and settings up to the limits of the machine's capabilities in order to achieve the AO Reference Voltage and AO nominal frequency. <1> Droop Mode. DER acts as a follower using Volt/VAR and Freq/Watt curves. | 2 | Isochronous Mode | Droop Mode. | DOPM DEXC |  | OpModIsld DrpV | SPC | GCF | DOPM DEXC.OpModIsld DrpV |  |  | New, added as corresponding BI. This combines two concepts: OpModIslk settings are 0 = grid connected,; 1 = islanded, while DEXC.DrpV is the droop mode
| BI21 | Sensed Grid Config Detection Enabled. If Enabled, the inverter may independently change its Active Settings Group based on locally observed grid conditions. <0> No Autonomous Detection. <1> Autonomous Detection. Inverter's Active Settings Group may differ from the Requested Settings Group | 2 | Not Ready | Ready |  |  | EnaCfgDet | SPC | DCTE | .EnaCfgDet |  | New | Note: If system is not in either local or lockout state, then it is in remote. Not clear what this is for or how used. There is no 61850 model yet
| BI25 | Storage Limit Units. Determines whether the storage Capacity Rating and Storage Reserve are set in units of Amp-hrs or Watt-hrs. If Amp-hrs is selected (the default), Capacity Rating and Storage Reserve are set using Battery AOs in amp-hrs. If Watt-hrs is selected, Capacity Rating and Storage Reserve using Battery AOs in Watt-hrs. | 2 | Amp-hrs (default) | Watt-hrs |  |  | n/a |  | DCTE | .n/a |  |  | New, added as corresponding BI. Not in 61850, and not sure if it needs to be??
| BI26 | Power factor excitation (operating quadrant) Here for IEC 61850 compatibility, not implemented | 2 | Producing VARs - Q1/Q2 | Absorbing VARs - Q3/Q4 | DRCT |  | PFExt | SPG | INV3 | DRCT.PFExt |  | X
| BI27 | Supports Low/High Voltage Ride-Through Mode | 0 | Supported | Not Supported | DVRT |  | Beh | ENS |  | DVRT.Beh | Yes | New
| BI28 | Supports Low/High Frequency Ride-Through Mode | 0 | Supported | Not Supported | DFRT |  | Beh | ENS |  | DFRT.Beh | Yes | New
| BI29 | Supports Dynamic Reactive Current Support Mode | 0 | Supported | Not Supported | RDGS |  | Beh | ENS | TV31 | RDGS.Beh | Yes | New
| BI30 | Supports Dynamic Volt-Watt Mode | 0 | Supported | Not Supported | DVWD |  | Beh | ENS |  | DVWD.Beh | Yes | Added per item 60
| BI31 | Supports Frequency-Watt Emergency Mode | 0 | Supported | Not Supported | FWHZ |  | Beh | ENS |  | FWHZ.Beh | Yes | New
| BI32 | Supports Active Power Limit Mode | 0 | Supported | Not Supported | DAMG |  | Beh | ENS | INV2 | DAMG.Beh | Yes | New | 61850 supports or doesn't support functions by either including or not including the LN. A possible alternate approach is to indicate the Beh DO as Off or On in the relevant LNs. With tentative agreement by WG17, I have proposed new LN names for these functions
| BI33 | Supports Charge/Discharge Mode | 0 | Supported | Not Supported | DCHA |  | Beh | ENS | INV4 | DCHA.Beh | Yes | New
| BI34 | Supports Coordinated Charge/Discharge Mode | 0 | Supported | Not Supported | DCBY |  | Beh | ENS |  | DCBY.Beh | Yes | New
| BI35 | Supports Peak Power Limiting Mode | 0 | Supported | Not Supported | DLFL |  | Beh | ENS | PPL | DLFL.Beh | Yes | New
| BI36 | Supports Load Following Mode | 0 | Supported | Not Supported | DGFL |  | Beh | ENS | LGF | DGFL.Beh | Yes | New
| BI37 | Supports Generation Following Mode | 0 | Supported | Not Supported | DGFL |  | Beh | ENS | LGF | DGFL.Beh | Yes | New
| BI38 | Supports Automatic Generation Control Mode | 0 | Supported | Not Supported | DCHA |  | Beh | ENS |  | DCHA.Beh | Yes | New | May need additional AGC-specific support DO in DCHA which is a more generic LN
| BI39 | Supports Active Power Smoothing Mode | 0 | Supported | Not Supported | DWSM |  | Beh | ENS | RPS | DWSM.Beh | Yes | New
| BI40 | Supports Volt-Watt Mode | 0 | Supported | Not Supported | DVWA DVVM |  | Beh | ENS | DVW | DVWA DVVM.Beh | Yes | New | May end up having tow LNs, one for available vars and one for max vars. Or they may be combined - don't know yet
| BI41 | Supports Frequency-Watt Smoothing Mode | 0 | Supported | Not Supported | DFWS |  | Beh | ENS |  | DFWS.Beh | Yes | New
| BI42 | Supports Fixed Power Factor Mode | 0 | Supported | Not Supported | DFPF |  | Beh | ENS | INV3 | DFPF.Beh | Yes | New
| BI43 | Supports Volt-VAR Control Mode | 0 | Supported | Not Supported | DVVC |  | Beh | ENS |  | DVVC.Beh | Yes | New
| BI44 | Supports Watt-VAr Mode | 0 | Supported | Not Supported | FPFW |  | Beh | ENS |  | FPFW.Beh | Yes | New
| BI45 | Supports Power Factor Correction Mode | 0 | Supported | Not Supported | DPFC |  | Beh | ENS |  | DPFC.Beh | Yes | New
| BI46 | Supports Pricing Mode | 0 | Supported | Not Supported | DPRG |  | Beh | ENS | INV5 | DPRG.Beh | Yes | New, added per item 56
| BI47 | Overvoltage Disconnect Protection Blocked | 1 | Not Blocked | Blocked (Disabled) | PTOV |  | Blk | SPS | MD | PTOV.Blk |  | New
| BI48 | Overvoltage Disconnect Protection Started | 1 | Not Started | Started (Evaluating) | PTOV |  | Str.general | ACD | MD | PTOV.Str.general |  | New
| BI49 | Overvoltage Disconnect Protection Operated | 1 | Not Operated | Operated (Disconnected) | PTOV |  | Op.general | ACT | MD | PTOV.Op.general |  | New
| BI50 | Undervoltage Disconnect Protection Blocked | 1 | Not Blocked | Blocked (Disabled) | PTUV |  | Blk | SPS | MD | PTUV.Blk |  | New
| BI51 | Undervoltage Disconnect Protection Started | 1 | Not Started | Started (Evaluating) | PTUV |  | Str.general | ACD | MD | PTUV.Str.general |  | New
| BI52 | Undervoltage Disconnect Protection Operated | 1 | Not Operated | Operated (Disconnected) | PTUV |  | Op.general | ACT | MD | PTUV.Op.general |  | New
| BI53 | Over Frequency Disconnect Protection Blocked | 1 | Not Blocked | Blocked (Disabled) | PTOV |  | Blk | SPS | MD | PTOV.Blk |  | New
| BI54 | Over Frequency Disconnect Protection Started | 1 | Not Started | Started (Evaluating) | PTOV |  | Str.general | ACD | MD | PTOV.Str.general |  | New
| BI55 | Over Frequency Disconnect Protection Operated | 1 | Not Operated | Operated (Disconnected) | PTOV |  | Op.general | ACT | MD | PTOV.Op.general |  | New
| BI56 | Under Frequency Disconnect Protection Blocked | 1 | Not Blocked | Blocked (Disabled) | PTUV |  | Blk | SPS | MD | PTUV.Blk |  | New
| BI57 | Under Frequency Disconnect Protection Started | 1 | Not Started | Started (Evaluating) | PTUV |  | Str.general | ACD | MD | PTUV.Str.general |  | New
| BI58 | Under Frequency Disconnect Protection Operated | 1 | Not Operated | Operated (Disconnected) | PTUV |  | Op.general | ACT | MD | PTUV.Op.general |  | New
| BI59 | Operating Mode - Low/High Voltage Ride-Through | 2 | Disabled | Enabled | DVRT |  | Mod | SPC |  | DVRT.Mod | Yes | New
| BI60 | Operating Mode - Low/High Frequency Ride-Through | 2 | Disabled | Enabled | DFRT |  | Mod | SPC |  |  | Yes | New
| BI61 | Operating Mode - Dynamic Reactive Current Support Enabled |  | Disabled | Enabled | RDGS |  | Mod | ENC |  | RDGS.Mod | Yes
| BI62 | Operating Mode - Dynamic Volt-Watt Enabled | 2 | Disabled | Enabled | DVWD |  | Mod | SPC |  | DVWD.Mod |  |  | Not in MESA
| BI63 | Operating Mode - Frequency-Watt Emergency Enabled | 2 | Disabled | Enabled | FWHZ |  | Mod | SPC |  | FWHZ.Mod | Yes | New
| BI64 | Operating Mode - Active Power Limit Enabled | 2 | Disabled | Enabled | DAMG |  | Mod | SPC | INV2 | DAMG.Mod | Yes | Used MESA name/description Could become DAMG.Mod | Same as "limited watts" If these modes are modeled as separate LNs, then the Data Object may (or may not) change to Mod within the LN shown under "supported"
| BI65 | Operating Mode - Charge/Discharge Enabled | 2 | Disabled | Enabled | DCHD |  | Mod | SPC | INV4 | DCHD.Mod | Yes
| BI66 | Operating Mode - Coordinated Charge / Discharge Management Enabled |  | Disabled | Enabled | DTCD |  | Mod | SPC |  | DTCD.Mod | Yes | New
| BI67 | Operating Mode - Peak Power Limiting Enabled | 2 | Disabled | Enabled | DPKP |  | Mod | SPC | PPL | DPKP.Mod | Yes | Used MESA name/description
| BI68 | Operating Mode - Load Following Enabled | 2 | Disabled | Enabled | DLFL |  | Mod | SPC | LGF | DLFL.Mod | Yes | Used "Load or Generation" name
| BI69 | Operating Mode - Generation Following Enabled | 2 | Disabled | Enabled | DGFL |  | Mod | SPC | LGF | DGFL.Mod | Yes |  | New since it was split from the Load Following
| BI70 | Operating Mode - Automatic Generation Control Enabled |  | Disabled | Enabled | DAGC |  | Mod | SPC |  | DAGC.Mod | Yes | New
| BI71 | Operating Mode - Active Power Smoothing Enabled | 2 | Disabled | Enabled | DWSM |  | Mod | SPC | RPS | DWSM.Mod | Yes
| BI72 | Operating Mode - Volt-Watt Enabled | 2 | Disabled | Enabled | DVWG |  | Mod | SPC | DVW | DVWG.Mod | Yes | Used MESA name/description
| BI73 | Operating Mode - Frequency-Watt Enabled |  | Disabled | Enabled | DFWS |  | Mod | SPC |  | DFWS.Mod | Yes | New
| BI74 | Operating Mode - Fixed Power Factor Enabled | 2 | Disabled | Enabled | DFPF |  | Mod | SPC | INV3 | DFPF.Mod | Yes
| BI75 | Operating Mode - Volt-VAR Control Enabled |  | Disabled | Enabled | DVVC |  | Mod | SPC |  | DVVC.Mod | Yes | New
| BI76 | Operating Mode - Watt-VAr Enabled |  | Disabled | Enabled | FPFW |  | Mod | SPC |  | FPFW.Mod | Yes | New
| BI77 | Operating Mode - Power Factor Correction Enabled |  | Disabled | Enabled | DPFC |  | Mod | SPC |  | DPFC.Mod | Yes | New
| BI78 | Operating Mode - Pricing Enabled |  | Disabled | Enabled | DPRG |  | Mod | SPC |  | DPRG.Mod |  | Per item #58 | Not in MESA
| BI79 | Dynamic Reactive Current Priority. Selects the priority of whether or not Watts should be curtailed in order to produce the reactive current required by this function. |  | Wattts can be curtailed in order to produce reactive current. | Watts can be curtailed in order to produce reactive current. | RDGS |  | VArMaxAvl | ENG |  | RDGS.VArMaxAvl | Yes | New added per MESA Word document | Volt-var has the ability to set available or maximum vars. Do we really need that same choice for this function?
| BI80 | Curve Enabled. The currently selected curve is enabled. | 2 | Disabled | Enabled | DGSM |  | ModEna | SPC | VV11-12 | DGSM.ModEna | Yes |  | New, added as corresponding BI
| S (S=84 for this version of the specifcation) | Selected Schedule Is Ready | 2 | Not Ready | Ready | FSCH |  | SchdSt.3 | ENS |  | FSCH.SchdSt.3 | Yes
| #REF! | Selected Schedule is Validated | 2 | Not validated | Validated | FSCH |  | SchdSt.2 | ENS |  | FSCH.SchdSt.2 | Yes
| S+1 | Selected Schedule Repeat Weekly Sunday | 2 | Do Not Repeat | Repeat | FSCH | xx | SchdReuse | SPG |  | FSCHxx.SchdReuse | Yes |  | Could establish an LN instance numbering scheme, such as 11 is Sunday, 12 is Monday, etc.
| #REF! | Selected Schedule Repeat Weekly Monday | 2 | Do Not Repeat | Repeat | FSCH | xx | SchdReuse | SPG |  | FSCHxx.SchdReuse | Yes
| #REF! | Selected Schedule Repeat Weekly Tuesday | 2 | Do Not Repeat | Repeat | FSCH | xx | SchdReuse | SPG |  | FSCHxx.SchdReuse | Yes
| S+2 | Selected Schedule Repeat Weekly Wednesday | 2 | Do Not Repeat | Repeat | FSCH | xx | SchdReuse | SPG |  | FSCHxx.SchdReuse | Yes
| S+3 | Selected Schedule Repeat Weekly Thursday | 2 | Do Not Repeat | Repeat | FSCH | xx | SchdReuse | SPG |  | FSCHxx.SchdReuse | Yes
| S+4 | Selected Schedule Repeat Weekly Friday | 2 | Do Not Repeat | Repeat | FSCH | xx | SchdReuse | SPG |  | FSCHxx.SchdReuse | Yes
| S+5 | Selected Schedule Repeat Weekly Saturday | 2 | Do Not Repeat | Repeat | FSCH | xx | SchdReuse | SPG |  | FSCHxx.SchdReuse | Yes
| S+6 | One or more Schedules Running | 2 | No schedule running | At least one schedule running | FSCC |  | ActSchdRef | ORS |  | FSCC.ActSchdRef | Yes | Added per item #105 | Indication of which schedule is active as an object reference. As long as no schedule is active the quality of the value is invalid.
| HM | Active power at Meter #1 is high | 1 | Normal | Alarm | MMXU | 2 | TotW.range | MV |  | MMXU2.TotW.range | Yes
| #REF! | Active power at Meter #1 is low | 1 | Normal | Alarm | MMXU | 2 | TotW.range | MV |  | MMXU2.TotW.range | Yes
| HM+1 | Reactive power at Meter #1 is high | 1 | Normal | Alarm | MMXU | 2 | TotVAr.range | MV |  | MMXU2.TotVAr.range | Yes
| #REF! | Reactive power at Meter #1 is low | 1 | Normal | Alarm | MMXU | 2 | TotVAr.range | MV |  | MMXU2.TotVAr.range | Yes
| #REF! | Power factor at Meter #1 is high | 1 | Normal | Alarm | MMXU | 2 | TotPF.range | MV |  | MMXU2.TotPF.range | Yes
| HM+2 | Power factor at Meter #1 is low | 1 | Normal | Alarm | MMXU | 2 | TotPF.range | MV |  | MMXU2.TotPF.range | Yes
| HM+3 | Phase A Voltage at Meter #1 is high | 1 | Normal | Alarm | MMXU | 2 | PhV.PhsA.range | WYE |  | MMXU2.PhV.PhsA.range | Yes | Fixed error - missing from basic profile
| HM+4 | Phase A Voltage at Meter #1 is low | 1 | Normal | Alarm | MMXU | 2 | PhV.PhsA.range | WYE |  |  | Yes | Fixed error - missing from basic profile
| HM+5 | Phase B Voltage at Meter #1 is high | 1 | Normal | Alarm | MMXU | 2 | PhV.PhsB.range | WYE |  | MMXU2.PhV.PhsB.range | Yes | Fixed error - missing from basic profile
| HM+6 | Phase B Voltage at Meter #1 is low | 1 | Normal | Alarm | MMXU | 2 | PhV.PhsB.range | WYE |  | MMXU2.PhV.PhsB.range | Yes | Fixed error - missing from basic profile
| HM+7 | Phase C Voltage at Meter #1 is high | 1 | Normal | Alarm | MMXU | 2 | PhV.PhsC.range | WYE |  | MMXU2.PhV.PhsC.range | Yes | Fixed error - missing from basic profile
| HM+8 | Phase C Voltage at Meter #1 is low | 1 | Normal | Alarm | MMXU | 2 | PhV.PhsC.range | WYE |  | MMXU2.PhV.PhsC.range | Yes | Fixed error - missing from basic profile
| HM+9 | Meter #1 Communication Error |  | Normal: No Active Communications Error | Alarm: Active Communications Error | LCCH |  | ChLiv | SPS |  | LCCH.ChLiv | Yes | new
| . . . | Meter #2 . . . Meter #m-1 points
| HM + mhbi (m-1) | Active power at Meter #m is high | 1 | Normal | Alarm | MMXU | 2 | TotW.range | MV |  | MMXU2.TotW.range
| #REF! | Active power at Meter #m is low | 1 | Normal | Alarm | MMXU | 2 | TotW.range | MV |  | MMXU2.TotW.range
| HM+ mhbi(m-1)+1 | Reactive power at Meter #m is high | 1 | Normal | Alarm | MMXU | 2 | TotVAr.range | MV |  | MMXU2.TotVAr.range
| #REF! | Reactive power at Meter #m is low | 1 | Normal | Alarm | MMXU | 2 | TotVAr.range | MV |  | MMXU2.TotVAr.range
| #REF! | Power factor at Meter #m is high | 1 | Normal | Alarm | MMXU | 2 | TotPF.range | MV |  | MMXU2.TotPF.range
| HM+ mhbi(m-1)+2 | Power factor at Meter #m is low | 1 | Normal | Alarm | MMXU | 2 | TotPF.range | MV
| HM+ mhbi(m-1)+3 | Phase A Voltage at Meter #m is high | 1 | Normal | Alarm | MMXU | 2 | PhV.PhsA.range | WYE |  | MMXU2.PhV.PhsA.range |  | Fixed error - missing from basic profile
| HM+ mhbi(m-1)+4 | Phase A Voltage at Meter #m is low | 1 | Normal | Alarm | MMXU | 2 | PhV.PhsA.range | WYE |  | MMXU2.PhV.PhsA.range |  | Fixed error - missing from basic profile
| HM+ mhbi(m-1)+5 | Phase B Voltage at Meter #m is high | 1 | Normal | Alarm | MMXU | 2 | PhV.PhsB.range | WYE |  | MMXU2.PhV.PhsB.range |  | Fixed error - missing from basic profile
| HM+ mhbi(m-1)+6 | Phase B Voltage at Meter #m is low | 1 | Normal | Alarm | MMXU | 2 | PhV.PhsB.range | WYE |  | MMXU2.PhV.PhsB.range |  | Fixed error - missing from basic profile
| HM+ mhbi(m-1)+7 | Phase C Voltage at Meter #m is high | 1 | Normal | Alarm | MMXU | 2 | PhV.PhsC.range | WYE |  | MMXU2.PhV.PhsC.range |  | Fixed error - missing from basic profile
| HM+ mhbi(m-1)+8 | Phase C Voltage at Meter #m is low | 1 | Normal | Alarm | MMXU | 2 | PhV.PhsC.range | WYE |  | MMXU2.PhV.PhsC.range |  | Fixed error - missing from basic profile
| HM+ mhbi(m-1)+9 | Meter #m Communication Error |  | Normal: No Active Communications Error | Alarm: Active Communications Error | LCCH |  | ChLiv | SPS |  | LCCH.ChLiv |  | new
| HDU | DER Unit #1 Is In Maintenance Operational State |  | Not in Maintenance | In Maintenance |  |  | GeStatSSL |  |  | .GeStatSSL | Yes | New, from MESA alarm set | Is this the same as Lockout State?
| #REF! | DER Unit #1 Has P1 Alarms |  | No P1 Alarms Active | Alarm: One or More P1 Alarms Active | CALH |  | GrAlm | SPS |  | CALH.GrAlm | Yes | New, from MESA alarm set | Which alarms to aggregate is not explicitly defined in 61850
| HDU +1 | DER Unit #1 Has P2 Alarms |  | No P2 Alarms Active | Alarm: One or More P2 Alarms Active | CALH |  | GrAlm | SPS |  | CALH.GrAlm | Yes | New, from MESA alarm set
| #REF! | DER Unit #1 Has P3 Alarms |  | No P3 Alarms Active | Alarm: One or More P3 Alarms Active | CALH |  | GrAlm | SPS |  | CALH.GrAlm | Yes | New, from MESA alarm set
| . . . | DER Unit #2 . . . DER Unit #e-1 points | [8 empty] | .
| HDU + duhbi(e-1) | DER Unit #e Is In Maintenance Operational State |  | Not in Maintenance | In Maintenance |  |  | GeModSSL |  |  | .GeModSSL |  | New, from MESA alarm set
| #REF! | DER Unit #e Has P1 Alarms |  | No P1 Alarms Active | Alarm: One or More P1 Alarms Active | CALH |  | GrAlm | SPS |  | CALH.GrAlm |  | New, from MESA alarm set
| HDU + duhbi(e-1)+1 | DER Unit #e Has P2 Alarms |  | No P2 Alarms Active | Alarm: One or More P2 Alarms Active | CALH |  | GrAlm | SPS |  | CALH.GrAlm |  | New, from MESA alarm set
| #REF! | DER Unit #e Has P3 Alarms |  | No P3 Alarms Active | Alarm: One or More P3 Alarms Active | CALH |  | GrAlm | SPS |  | CALH.GrAlm |  | New, from MESA alarm set
| HI | Inverter #1 active power output too high | 1 | Normal | Alarm | MMXU | 1 | TotW.range | MV |  | MMXU1.TotW.range | Yes
| #REF! | Inverter #1 active power output too low | 1 | Normal | Alarm | MMXU | 1 | TotW.range | MV |  | MMXU1.TotW.range | Yes
| HI+1 | Inverter #1 reactive output too high | 1 | Normal | Alarm | MMXU | 1 | TotVAr.range | MV |  |  | Yes
| #REF! | Inverter #1 reactive output too low | 1 | Normal | Alarm | MMXU | 1 | TotVAr.range | MV |  | MMXU1.TotVAr.range | Yes
| #REF! | Inverter #1 Current output frequency is too high | 1 | Normal | Alarm | MMXU | 1 | Hz.range | MV |  | MMXU1.Hz.range | Yes
| HI+2 | Inverter #1 Current output frequency is too low | 1 | Normal | Alarm | MMXU | 1 | Hz.range | MV |  | MMXU1.Hz.range | Yes
| HI+3 | Inverter #1 DC input power too high | 1 | Normal | Alarm | MMDC | 1 | Watt.range | MV |  | MMDC1.Watt.range | Yes
| HI+4 | Inverter #1 DC input power too low | 1 | Normal | Alarm | MMDC | 1 | Watt.range | MV |  | MMDC1.Watt.range | Yes
| HI+5 | Inverter #1 DC current level too high | 1 | Normal | Alarm | MMDC | 1 | Amp.range | MV |  |  | Yes
| HI+6 | Inverter #1 DC current level too low | 1 | Normal | Alarm | MMDC | 1 | Amp.range | MV |  | MMDC1.Amp.range | Yes
| HI+7 | Inverter #1 DC voltage at PCS too low | 1 | Normal | Alarm | MMDC | 1 | Vol.range | MV |  | MMDC1.Vol.range | Yes
| HI+8 | Inverter #1 DC voltage at PCS too high | 1 | Normal | Alarm | MMDC | 1 | Vol.range | MV |  | MMDC1.Vol.range | Yes | Fixed error in description
| HI+9 | Inverter #1 DNP3 Power Factor Excitation (Operating Quadrant) | 1 | Overexcited (producing VARs - Q1/Q2) | Underexcited (absorbing VARs - Q3/Q4) | DRCT | 1 | PFExt | SPG | INV3 | DRCT1.PFExt | Yes | New | Should we use this?
| HI+10 | Inverter #1 Is DC Contactor Closed |  | Normal | Alarm |  |  | #SClosedIIC |  |  | .#SClosedIIC | Yes | New, per item 40 | There is probably a DO, but I don't know what it is
| HI+11 | Inverter #1 Ground Fault Alarm |  | Normal | Alarm |  |  | #SAlarGGF |  |  | .#SAlarGGF | Yes | New, per item 40 | There is probably a DO, but I don't know what it is
| HI+12 | Inverter #1 DC Over Voltage Alarm |  | Normal | Alarm | MMDC |  | Vol.range | MV |  | MMDC.Vol.range | Yes | New, per item 40
| HI+13 | Inverter #1 DC Under Voltage Alarm |  | Normal | Alarm | MMDC |  | Vol.range | MV |  | MMDC.Vol.range | Yes | New, per item 44
| HI+14 | Inverter #1 AC Disconnect Warning |  | Normal | Alarm |  |  | #SWarninACACD |  |  |  | Yes | New, per item 40 | Sporadic DOs in historical, since many of these are not in 61850 for an inverter, but may use the protection LNs?? Same for battery historical points
| HI+15 | Inverter #1 DC Disconnect Warning |  | Normal | Alarm |  |  | #SWarninDCDCD |  |  | .#SWarninDCDCD | Yes | New, per item 40
| HI+16 | Inverter #1 Grid Disconnect Warning |  | Normal | Inverter does not detect power on the grid | DINV |  | GriModSt | ENS |  | DINV.GriModSt | Yes | New, per item 40
| HI+17 | Inverter #1 Cabinet Open Warning |  | Normal | Alarm |  |  | #SWarninCCO |  |  | .#SWarninCCO | Yes | New, per item 41
| HI+18 | Inverter #1 Manual Shutdown Warning |  | Normal | Alarm |  |  | #SWarninMMS |  |  | .#SWarninMMS | Yes | New, per item 41
| HI+19 | Inverter #1 Over Temperature Alarm |  | Normal | Alarm | DINV |  | EnclTmp.range | MV |  | DINV.EnclTmp.range | Yes | New, per item 41
| HI+20 | Inverter #1 Under Temperature Alarm |  | Normal | Alarm | DINV |  | EnclTmp.range | MV |  | DINV.EnclTmp.range | Yes | New, per item 41
| HI+21 | Inverter #1 Over Frequency Alarm |  | Normal | Alarm | MMXU | 1 | Hz.range | MV |  | MMXU1.Hz.range | Yes | New, per item 41
| HI+23 | Inverter #1 Under Frequency Alarm |  | Normal | Alarm | MMXU | 1 | Hz.range | MV |  | MMXU1.Hz.range | Yes | New, per item 41
| HI+24 | Inverter #1 AC Over Voltage Alarm |  | Normal | Alarm | MMXU |  | PhV.PhsA.range | WYE |  | MMXU.PhV.PhsA.range | Yes | New, per item 41
| HI+25 | Inverter #1 AC Under Voltage Alarm |  | Normal | Alarm | MMXU |  | PhV.PhsA.range | WYE |  | MMXU.PhV.PhsA.range | Yes | New, per item 41
| HI+22 | Inverter #1 Blown String Fuse Alarm |  | Normal | Alarm | XFUS |  | FuSt | SPS |  | XFUS.FuSt | Yes | New, per item 41
| HI+26 | Inverter #1 Memory Loss Alarm |  | Normal | Alarm |  |  | #SAlarMML |  |  | .#SAlarMML | Yes | New, per item 41
| HI+27 | Inverter #1 Hardware Test Failure |  | Normal | Alarm |  |  | #SFailurHHT |  |  | .#SFailurHHT | Yes | New, per item 41
| HI+28 | Inverter #1 Other Alarm |  | Normal | Alarm | CALH |  | GrAlm | SPS |  | CALH.GrAlm | Yes | New, per item 41
| HI+29 | Inverter #1 Other Warning |  | Normal | Alarm | CALH |  | GrWrn | SPS |  | CALH.GrWrn | Yes | New, per item 41
| . . . | Inverter #2 . . . Inverter #p-1 points |  | Normal
| HI+ ihbi(p-1) | Inverter #p active power output too high | 1 | Normal | Alarm | MMXU | 1 | TotW.range | MV |  | MMXU1.TotW.range
| #REF! | Inverter #p active power output too low | 1 | Normal | Alarm | MMXU | 1 | TotW.range | MV |  | MMXU1.TotW.range
| HI+ ihbi(p-1)+1 | Inverter #p reactive output too high | 1 | Normal | Alarm | MMXU | 1 | TotVAr.range | MV |  | MMXU1.TotVAr.range
| #REF! | Inverter #p reactive output too low | 1 | Normal | Alarm | MMXU | 1 | TotVAr.range | MV |  | MMXU1.TotVAr.range
| #REF! | Inverter #p current output frequency is too high | 1 | Normal | Alarm | MMXU | 1 | Hz.range | MV |  | MMXU1.Hz.range
| HI+ ihbi(p-1)+2 | Inverter #p current output frequency is too low | 1 | Normal | Alarm | MMXU | 1 | Hz.range | MV |  | MMXU1.Hz.range
| HI+ ihbi(p-1)+3 | Inverter #p DC input power too high | 1 | Normal | Alarm | MMDC | 1 | Watt.range | MV
| HI+ ihbi(p-1)+4 | Inverter #p DC input power too low | 1 | Normal | Alarm | MMDC | 1 | Watt.range | MV |  | MMDC1.Watt.range
| HI+ ihbi(p-1)+5 | Inverter #p DC current level too high | 1 | Normal | Alarm | MMDC | 1 | Amp.range | MV |  | MMDC1.Amp.range
| HI+ ihbi(p-1)+6 | Inverter #p DC current level too low | 1 | Normal | Alarm | MMDC | 1 | Amp.range | MV |  | MMDC1.Amp.range
| HI+ ihbi(p-1)+7 | Inverter #p DC voltage at PCS too low | 1 | Normal | Alarm | MMDC | 1 | Vol.range | MV |  | MMDC1.Vol.range
| HI+ ihbi(p-1)+8 | Inverter #p DC voltage at PCS too high | 1 | Normal | Alarm | MMDC | 1 | Vol.range | MV |  | MMDC1.Vol.range |  | Fixed error in description
| HI+ ihbi(p-1)+9 | Inverter #p DNP3 Power Factor Excitation (Operating Quadrant) | 1 | Overexcited (producing VARs - Q1/Q2) | Underexcited (absorbing VARs - Q3/Q4) | DRCT | 1 | PFExt | SPG | INV3 | DRCT1.PFExt |  | New | Should we use this?
| HI+ ihbi(p-1)+10 | Inverter #p Is DC Contactor Closed |  | Normal | Alarm |  |  | #SClosedIIC |  |  | .#SClosedIIC |  | New, per item 40
| HI+ ihbi(p-1)+11 | Inverter #p Ground Fault Alarm |  | Normal | Alarm |  |  | #SAlarGGF |  |  |  |  | New, per item 40
| HI+ ihbi(p-1)+12 | Inverter #p DC Over Voltage Alarm |  | Normal | Alarm | MMDC |  | Vol.range | MV |  | MMDC.Vol.range |  | New, per item 40
| HI+ ihbi(p-1)+13 | Inverter #p DC Under Voltage Alarm |  | Normal | Alarm | MMDC |  | Vol.range | MV |  | MMDC.Vol.range |  | New, per item 44
| HI+ ihbi(p-1)+14 | Inverter #p AC Disconnect Warning |  | Normal | Alarm |  |  | #SWarninACACD |  |  | .#SWarninACACD |  | New, per item 40
| HI+ ihbi(p-1)+15 | Inverter #p DC Disconnect Warning |  | Normal | Alarm |  |  | #SWarninDCDCD |  |  | .#SWarninDCDCD |  | New, per item 40
| HI+ ihbi(p-1)+16 | Inverter #p Grid Disconnect Warning |  | Normal | Inverter does not detect power on the grid |  |  | #SWarninGGD |  |  | .#SWarninGGD |  | New, per item 40
| HI+ ihbi(p-1)+17 | Inverter #p Cabinet Open Warning |  | Normal | Alarm |  |  | #SWarninCCO |  |  | .#SWarninCCO |  | New, per item 41
| HI+ ihbi(p-1)+18 | Inverter #p Manual Shutdown Warning |  | Normal | Alarm |  |  | #SWarninMMS |  |  | .#SWarninMMS |  | New, per item 41
| HI+ ihbi(p-1)+19 | Inverter #p Over Temperature Alarm |  | Normal | Alarm | DINV |  | EnclTmp.range | MV |  | DINV.EnclTmp.range |  | New, per item 41
| HI+ ihbi(p-1)+20 | Inverter #p Under Temperature Alarm |  | Normal | Alarm | DINV |  | EnclTmp.range | MV |  | DINV.EnclTmp.range |  | New, per item 41
| HI+ ihbi(p-1)+21 | Inverter #p Over Frequency Alarm |  | Normal | Alarm | MMXU | 1 | Hz.range | MV |  | MMXU1.Hz.range |  | New, per item 41
| HI+ ihbi(p-1)+23 | Inverter #p Under Frequency Alarm |  | Normal | Alarm | MMXU | 1 | Hz.range | MV |  | MMXU1.Hz.range |  | New, per item 41
| HI+ ihbi(p-1)+24 | Inverter #p AC Over Voltage Alarm |  | Normal | Alarm | MMXU |  | PhV.PhsA.range | WYE |  | MMXU.PhV.PhsA.range |  | New, per item 41
| HI+ ihbi(p-1)+25 | Inverter #p AC Under Voltage Alarm |  | Normal | Alarm | MMXU |  | PhV.PhsA.range | WYE |  | MMXU.PhV.PhsA.range |  | New, per item 41
| HI+ ihbi(p-1)+22 | Inverter #p Blown String Fuse Alarm |  | Normal | Alarm | XFUS |  | FuSt | SPS |  | XFUS.FuSt |  | New, per item 41
| HI+ ihbi(p-1)+26 | Inverter #p Memory Loss Alarm |  | Normal | Alarm |  |  | #SAlarMML |  |  | .#SAlarMML |  | New, per item 41
| HI+ ihbi(p-1)+27 | Inverter #p Hardware Test Failure |  | Normal | Alarm |  |  | #SFailurHHT |  |  | .#SFailurHHT |  | New, per item 41
| HI+ ihbi(p-1)+28 | Inverter #p Other Alarm |  | Normal | Alarm | CALH |  | GrAlm | SPS |  | CALH.GrAlm |  | New, per item 41
| HI+ ihbi(p-1)+29 | Inverter #p Other Warning |  | Normal | Alarm | CALH |  | GrWrn | SPS |  | CALH.GrWrn |  | New, per item 41
| HB | Status of storage for Battery #1 | 3 | Dis-connected | Connected | DBAT | 1 | BatSt | SPC |  | DBAT1.BatSt |  |  | Included because mandatory. Should it also imply that it is discharging?
| #REF! | External Battery #1 voltage (between battery charger and battery) is too high | 1 | Normal | Alarm | DBAT | 1 | Vol.range | MV |  | DBAT1.Vol.range
| HB+1 | External Battery #1 voltage (between battery charger and battery) is too low | 1 | Normal | Alarm | DBAT | 1 | Vol.range | MV |  | DBAT1.Vol.range
| #REF! | Internal Battery #1 voltage is too low | 1 | Normal | Alarm | DBAT | 1 | InBatV | MV |  | DBAT1.InBatV |  | Fixed error in description
| #REF! | Internal Battery #1 voltage is too high | 1 | Normal | Alarm | DBAT | 1 | InBatV | MV
| HB+2 | Battery Bank #1 Communication Error |  | Normal | Alarm | LCCH |  | ChLiv | SPS |  | LCCH.ChLiv |  | New, per item 42 | fmc stopped here
| HB+3 | Battery Bank #1 Is In Local Control Mode |  | Normal | Alarm |  |  | EtModBBC |  |  | .EtModBBC |  | New, per item 42
| HB+4 | Battery Bank #1 Is DC Contactor Closed |  | Normal | Alarm |  |  | EtCloseBBC |  |  | .EtCloseBBC |  | New, per item 42
| HB+5 | Battery Bank #1 Is Charging |  | Normal | Alarm | DBTC |  | BatChaSt | ENS |  | DBTC.BatChaSt |  | New, per item 42
| HB+6 | Battery Bank #1 Is Discharging |  | Normal | Alarm | DBAT | 1 | BatSt | SPC |  | DBAT1.BatSt |  | New, per item 42
| HB+7 | Battery Bank #1 Over Temperature Alarm |  | Normal | Alarm |  |  | EtAlarBBT |  |  | .EtAlarBBT |  | New, per item 42
| HB+8 | Battery Bank #1 Under Temperature Alarm |  | Normal | Alarm |  |  | EtAlarBBT |  |  | .EtAlarBBT |  | New, per item 42
| HB+9 | Battery Bank #1 Over Ambient Temperature Warning |  | Normal | Alarm |  |  | EtWarninBBT |  |  | .EtWarninBBT |  | New, per item 49
| HB+10 | Battery Bank #1 Under Ambient Temperature Warning |  | Normal | Alarm |  |  | EtWarninBBT |  |  | .EtWarninBBT |  | New, per item 49
| HB+11 | Battery Bank #1 Over Charge Current Alarm |  | Normal | Alarm |  |  | EtAlarBBC |  |  | .EtAlarBBC |  | New, per item 42
| HB+12 | Battery Bank #1 Over Discharge Current Alarm |  | Normal | Alarm |  |  | EtAlarBBC |  |  | .EtAlarBBC |  | New, per item 42
| HB+13 | Battery Bank #1 Over Charge Current Warning |  | Normal | Alarm |  |  | EtWarninBBC |  |  | .EtWarninBBC |  | New, per item 42
| HB+14 | Battery Bank #1 Over Discharge Current Warning |  | Normal | Alarm |  |  | EtWarninBBC |  |  | .EtWarninBBC |  | New, per item 42
| HB+15 | Battery Bank #1 Voltage Imbalance Warning |  | Normal | Alarm |  |  | EtWarninBBI |  |  | .EtWarninBBI |  | New, per item 42
| HB+16 | Battery Bank #1 Current Imbalance Warning |  | Normal | Alarm |  |  | EtWarninBBI |  |  | .EtWarninBBI |  | New, per item 42
| HB+17 | Battery Bank #1 Over Voltage Alarm |  | Normal | Alarm |  |  | EtBBV |  |  | .EtBBV |  | New, per item 42
| HB+18 | Battery Bank #1 Under Voltage Alarm |  | Normal | Alarm |  |  | EtAlarBBV |  |  | .EtAlarBBV |  | New, per item 42
| HB+19 | Battery Bank #1 Over Voltage Warning |  | Normal | Alarm |  |  | EtBBV |  |  | .EtBBV |  | New, per item 42
| HB+20 | Battery Bank #1 Under Voltage Warning |  | Normal | Alarm |  |  | EtWarninBBV |  |  | .EtWarninBBV |  | New, per item 42
| HB+21 | Battery Bank #1 Contactor Failure |  | Normal | Alarm |  |  | EtFaiBBC |  |  | .EtFaiBBC |  | New, per item 42
| HB+23 | Battery Bank #1 Fan Error |  | Normal | Alarm |  |  | EtErroBBF |  |  | .EtErroBBF |  | New, per item 42
| HB+24 | Battery Bank #1 Ground Fault |  | Normal | Alarm |  |  | EtFaulBBG |  |  | .EtFaulBBG |  | New, per item 42
| HB+25 | Battery Bank #1 Safety Fault |  | Normal | Alarm |  |  | EtFaulBBS |  |  | .EtFaulBBS |  | New, per item 42
| HB+22 | Battery Bank #1 Other Alarm |  | Normal | Alarm |  |  | EtAlarBBO |  |  | .EtAlarBBO |  | New, per item 42
| HB+26 | Battery Bank #1 Other Warning |  | Normal | Alarm |  |  | EtWarningBBO |  |  | .EtWarningBBO |  | New, per item 42
| HB+27 | Battery Bank #1 Fire Alarm |  | Normal | Alarm |  |  | EtAlarBBF |  |  | .EtAlarBBF |  | New, per item 42
| HB+28 | Battery Bank #1 Fire Supervisory Warning |  | Normal | Alarm |  |  | EtWarninBBS |  |  | .EtWarninBBS |  | New, per item 42
| HB+29 | Battery Bank #1 Fire Trouble Warning |  | Normal | Alarm |  |  | EtBBT |  |  | .EtBBT |  | New, per item 42
| HB+30 | Battery Bank #1 Fire Power Fault Warning |  | Normal | Alarm |  |  | EtWarninBBF |  |  | .EtWarninBBF |  | New, per item 42
| HB+31 | Battery Bank #1 Chiller Alarm |  | Normal | Alarm |  |  | EtAlarmBBC |  |  | .EtAlarmBBC |  | New, per item 42
| HB+37 | Battery Bank #1 Chiller Warning |  | Normal | Alarm |  |  | EtWarniBBC |  |  | .EtWarniBBC |  | New, per item 42
| HB+32 | Battery Bank #1 Air Handler Alarm |  | Normal | Alarm |  |  | EtABBH |  |  | .EtABBH |  | New, per item 42
| HB+33 | Battery Bank #1 Air Handler Warning |  | Normal | Alarm |  |  | EtWBBH |  |  | .EtWBBH |  | New, per item 42
| HB+34 | Battery Bank #1 Fluid Alarm |  | Normal | Alarm |  |  | EtAlarBBF |  |  | .EtAlarBBF |  | New, per item 42
| HB+36 | Battery Bank #1 Fluid Warning |  | Normal | Alarm |  |  | EtWarningBBF |  |  | .EtWarningBBF |  | New, per item 42
| HB+38 | Battery Bank #1 Gas Alarm |  | Normal | Alarm |  |  | EtAlarBBG |  |  | .EtAlarBBG |  | New, per item 42
| HB+40 | Battery Bank #1 Gas Warning |  | Normal | Alarm |  |  | EtWarninBBG |  |  | .EtWarninBBG |  | New, per item 42
| HB+41 | Battery Bank #1 Electrolyte Alarm |  | Normal | Alarm |  |  | EtABBE |  |  | .EtABBE |  | New, per item 42
| HB+44 | Battery Bank #1 Electrolyte Warning |  | Normal | Alarm |  |  | EtWBBE |  |  | .EtWBBE |  | New, per item 42
| HB+45 | Battery Bank #1 Electrical Alarm |  | Normal | Alarm |  |  | EtAlBBE |  |  | .EtAlBBE |  | New, per item 42
| HB+35 | Battery Bank #1 Electrical Warning |  | Normal | Alarm |  |  | EtWaBBE |  |  | .EtWaBBE |  | New, per item 42
| . . . | Battery Bank #2 . . . Battery Bank #b-1 points | [8 empty] | .
| HB+ bhbi(b-1) | Status of storage for Battery #b | 3 | Off | On | ZBAT | 1 | BatSt | SPC |  | ZBAT1.BatSt |  |  | Included because mandatory
| #REF! | External Battery #b voltage (between battery charger and battery) is too high | 1 | Normal | Alarm | ZBAT | 1 | Vol.range | MV |  | ZBAT1.Vol.range
| HB+ bhbi(b-1)+1 | External Battery #b voltage (between battery charger and battery) is too low | 1 | Normal | Alarm | ZBAT | 1 | Vol.range | MV |  | ZBAT1.Vol.range
| #REF! | Internal Battery #b voltage is too low | 1 | Normal | Alarm | ZBAT | 1 | InBatV | MV |  | ZBAT1.InBatV |  | Fixed error in description
| #REF! | Internal Battery #b voltage is too high | 1 | Normal | Alarm | ZBAT | 1 | InBatV | MV |  | ZBAT1.InBatV
| HB+ bhbi(b-1)+2 | Battery Bank #b Communication Error |  | Normal | Alarm | [5 empty] | . |  | New, per item 42
| HB+ bhbi(b-1)+3 | Battery Bank #b Is In Local Control Mode |  | Normal | Alarm |  |  | EtModBBC |  |  | .EtModBBC |  | New, per item 42
| HB+ bhbi(b-1)+4 | Battery Bank #b Is DC Contactor Closed |  | Normal | Alarm |  |  | EtCloseBBC |  |  | .EtCloseBBC |  | New, per item 42
| HB+ bhbi(b-1)+5 | Battery Bank #b Is Charging |  | Normal | Alarm |  |  | EtCharginBBI |  |  | .EtCharginBBI |  | New, per item 42
| HB+ bhbi(b-1)+6 | Battery Bank #b Is Discharging |  | Normal | Alarm |  |  | EtDischarginBBI |  |  | .EtDischarginBBI |  | New, per item 42
| HB+ bhbi(b-1)+7 | Battery Bank #b Over Temperature Alarm |  | Normal | Alarm |  |  | EtAlarBBT |  |  | .EtAlarBBT |  | New, per item 42
| HB+ bhbi(b-1)+8 | Battery Bank #b Under Temperature Alarm |  | Normal | Alarm |  |  | EtAlarBBT |  |  | .EtAlarBBT |  | New, per item 42
| HB+ bhbi(b-1)+9 | Battery Bank #b Over Ambient Temperature Warning |  | Normal | Alarm |  |  | EtWarninBBT |  |  | .EtWarninBBT |  | New, per item 49
| HB+ bhbi(b-1)+10 | Battery Bank #b Under Ambient Temperature Warning |  | Normal | Alarm |  |  | EtWarninBBT |  |  | .EtWarninBBT |  | New, per item 49
| HB+ bhbi(b-1)+11 | Battery Bank #b Over Charge Current Alarm |  | Normal | Alarm |  |  | EtAlarBBC |  |  | .EtAlarBBC |  | New, per item 42
| HB+ bhbi(b-1)+12 | Battery Bank #b Over Discharge Current Alarm |  | Normal | Alarm |  |  | EtAlarBBC |  |  | .EtAlarBBC |  | New, per item 42
| HB+ bhbi(b-1)+13 | Battery Bank #b Over Charge Current Warning |  | Normal | Alarm |  |  | EtWarninBBC |  |  | .EtWarninBBC |  | New, per item 42
| HB+ bhbi(b-1)+14 | Battery Bank #b Over Discharge Current Warning |  | Normal | Alarm |  |  | EtWarninBBC |  |  | .EtWarninBBC |  | New, per item 42
| HB+ bhbi(b-1)+15 | Battery Bank #b Voltage Imbalance Warning |  | Normal | Alarm |  |  | EtWarninBBI |  |  | .EtWarninBBI |  | New, per item 42
| HB+ bhbi(b-1)+16 | Battery Bank #b Current Imbalance Warning |  | Normal | Alarm |  |  | EtWarninBBI |  |  | .EtWarninBBI |  | New, per item 42
| HB+ bhbi(b-1)+17 | Battery Bank #b Over Voltage Alarm |  | Normal | Alarm |  |  | EtBBV |  |  | .EtBBV |  | New, per item 42
| HB+ bhbi(b-1)+18 | Battery Bank #b Under Voltage Alarm |  | Normal | Alarm |  |  | EtAlarBBV |  |  | .EtAlarBBV |  | New, per item 42
| HB+ bhbi(b-1)+19 | Battery Bank #b Over Voltage Warning |  | Normal | Alarm |  |  | EtBBV |  |  | .EtBBV |  | New, per item 42
| HB+ bhbi(b-1)+20 | Battery Bank #b Under Voltage Warning |  | Normal | Alarm |  |  | EtWarninBBV |  |  | .EtWarninBBV |  | New, per item 42
| HB+ bhbi(b-1)+21 | Battery Bank #b Contactor Failure |  | Normal | Alarm |  |  | EtFaiBBC |  |  | .EtFaiBBC |  | New, per item 42
| HB+ bhbi(b-1)+23 | Battery Bank #b Fan Error |  | Normal | Alarm |  |  | EtErroBBF |  |  | .EtErroBBF |  | New, per item 42
| HB+ bhbi(b-1)+24 | Battery Bank #b Ground Fault |  | Normal | Alarm |  |  | EtFaulBBG |  |  | .EtFaulBBG |  | New, per item 42
| HB+ bhbi(b-1)+25 | Battery Bank #b Safety Fault |  | Normal | Alarm |  |  | EtFaulBBS |  |  | .EtFaulBBS |  | New, per item 42
| HB+ bhbi(b-1)+22 | Battery Bank #b Other Alarm |  | Normal | Alarm |  |  | EtAlarBBO |  |  | .EtAlarBBO |  | New, per item 42
| HB+ bhbi(b-1)+26 | Battery Bank #b Other Warning |  | Normal | Alarm |  |  | EtWarningBBO |  |  | .EtWarningBBO |  | New, per item 42
| HB+ bhbi(b-1)+27 | Battery Bank #b Fire Alarm |  | Normal | Alarm |  |  | EtAlarBBF |  |  | .EtAlarBBF |  | New, per item 42
| HB+ bhbi(b-1)+28 | Battery Bank #b Fire Supervisory Warning |  | Normal | Alarm |  |  | EtWarninBBS |  |  | .EtWarninBBS |  | New, per item 42
| HB+ bhbi(b-1)+29 | Battery Bank #b Fire Trouble Warning |  | Normal | Alarm |  |  | EtBBT |  |  | .EtBBT |  | New, per item 42
| HB+ bhbi(b-1)+30 | Battery Bank #b Fire Power Fault Warning |  | Normal | Alarm |  |  | EtWarninBBF |  |  | .EtWarninBBF |  | New, per item 42
| HB+ bhbi(b-1)+31 | Battery Bank #b Chiller Alarm |  | Normal | Alarm |  |  | EtAlarmBBC |  |  | .EtAlarmBBC |  | New, per item 42
| HB+ bhbi(b-1)+37 | Battery Bank #b Chiller Warning |  | Normal | Alarm |  |  | EtWarniBBC |  |  | .EtWarniBBC |  | New, per item 42
| HB+ bhbi(b-1)+32 | Battery Bank #b Air Handler Alarm |  | Normal | Alarm |  |  | EtABBH |  |  | .EtABBH |  | New, per item 42
| HB+ bhbi(b-1)+33 | Battery Bank #b Air Handler Warning |  | Normal | Alarm |  |  | EtWBBH |  |  | .EtWBBH |  | New, per item 42
| HB+ bhbi(b-1)+34 | Battery Bank #b Fluid Alarm |  | Normal | Alarm |  |  | EtAlarBBF |  |  | .EtAlarBBF |  | New, per item 42
| HB+ bhbi(b-1)+36 | Battery Bank #b Fluid Warning |  | Normal | Alarm |  |  | EtWarningBBF |  |  | .EtWarningBBF |  | New, per item 42
| HB+ bhbi(b-1)+38 | Battery Bank #b Gas Alarm |  | Normal | Alarm |  |  | EtAlarBBG |  |  | .EtAlarBBG |  | New, per item 42
| HB+ bhbi(b-1)+40 | Battery Bank #b Gas Warning |  | Normal | Alarm |  |  | EtWarninBBG |  |  | .EtWarninBBG |  | New, per item 42
| HB+ bhbi(b-1)+41 | Battery Bank #b Electrolyte Alarm |  | Normal | Alarm |  |  | EtABBE |  |  | .EtABBE |  | New, per item 42
| HB+ bhbi(b-1)+44 | Battery Bank #b Electrolyte Warning |  | Normal | Alarm |  |  | EtWBBE |  |  | .EtWBBE |  | New, per item 42
| HB+ bhbi(b-1)+45 | Battery Bank #b Electrical Alarm |  | Normal | Alarm |  |  | EtAlBBE |  |  | .EtAlBBE |  | New, per item 42
| HB+ bhbi(b-1)+35 | Battery Bank #b Electrical Warning |  | Normal | Alarm |  |  | EtWaBBE |  |  | .EtWaBBE |  | New, per item 42

## BO
Temp | Point Index | Name / Description | Select/Operate | Direct Operate | Direct Operate – No Ack | Pulse On | Pulse Off | Latch On | Latch Off | Trip | Close | Count > 1 | Cancel Current Operation | Name for State when value is 0 | Name for State when value is 1 | Default Cmd Class | Default Event Class | LN Class | LN Inst | Data Object | CDC | Function | Unique String | MESA-ESS | Note 1 | Note 2
| #REF! | System Set Lockout State | X | X | X | X | X | X | X | X | X |  |  | Not Locked Out | Lock Out | 2 | 2 | [5 empty] | . | Yes
| BO0 | Set Local State | X | X | X | X | X | X | X | X | X |  |  | Remote (Not local) | Local | [7 empty] | . | Yes | New, included for consistency i.e. each mode has a "Enable" status BO
| #REF! | Set DER System Automatic State | X | X | X | X | X | X | X | X | X |  |  | Not Auto | Auto | 2 | 2 | DRCC |  | AutoManCtl | SPC |  | DRCC.AutoManCtl | Yes |  | Included because mandatory. Included per item 53
| #REF! | System Initiate Start-up Sequence (Return to Service) Setting this to 1 does the following: - Sets BI "System Is Starting Up" to 1 indicating that the system is starting up. Additional start-up status can be found in AI "System Start-up Status". - Instructs all batteries to connect. - Once each battery has reported that it has connect successfully, instructs corresponding PCS to start. System can be shut down by executing B0 "Emergency Stop" command. This operation is the same as California Rule 21 "Soft Start". | X | X | X | X | X | X | X | X | X |  |  | Non-Operational | Initiate Start-up | 2 | 2 | DRCC |  | DERStr | SPC |  | DRCC.DERStr | Yes
| BO1 | System Execute Stop. Setting this to 1 does the following: - Sets BI "System Is Emergency Stopping" to 1 indicating that an emergency stop is in progress. - Ensures that any executing operating modes are shut down (disabled). - Ensures that any executing schedules are shut down (disabled). - Instructs all inverters to shut down. - Instructs all batteries to disconnect. System can be started again by executing BO "Initiate Start-up Sequence" command. | X | X | X | X | X | X | X | X | X |  |  | No Change | Stop (Emergency) | 2 | 2 | DRCC |  | DERStop | SPC |  | DRCC.DERStop | Yes
| BO2 | System Permission to Start | X | X | X | X | X | X | X | X | X |  |  | DCTE | Start Permission Granted | 2 | 2 | DRCC |  | DERStrAuth | SPC |  | DRCC.DERStrAuth | Yes | Made description more general | Is this really a status, not a command?
| BO3 | System Permission to Stop | X | X | X | X | X | X | X | X | X |  |  | DCTE | Stop Permission Granted | 2 | 2 | DRCC |  | DERStopSuth | SPC |  | DRCC.DERStopSuth | Yes | Made description more general | Is this really a status, not a command?
| BO4 | DER connect/ disconnect switch | X | X | X | X | X | X | X | X | X |  |  | Open Switch | Close Switch | 2 |  | CSWI |  | Pos | DPC | INV1 | CSWI. Pos | Yes |  | Keep per item #50
| BO5 | Enable Sensed Grid Config Detection. If Enabled, the DER may independently change its Active Settings Group based on locally observed grid conditions. <0> No Autonomous Detection. <1> Autonomous Detection. Inverter's Active Settings Group may differ from the Requested Settings Group | X | X | X | X | X | X | X | X | X |  |  | No Autonomous Detection | Autonomous Detection | 2 | 2 |  |  | EnaCfgDet | SPC | GCF | .EnaCfgDet |  | New
| BO6 | Islanded Mode. Determines how the DER behaves when in an Islanded configuration. <0> Isochronous Mode. DER attempts to control voltage and frequency independent of configured curves and settings up to the limits of the machine's capabilities in order to achieve AO reference voltage and AO nominal frequency. <1> Droop Mode. DER acts as a follower using Volt/VAR and Freq/Watt curves. | X | X | X | X | X | X | X | X | X |  |  | sochronous Mode | Droop Mode | 2 | 2 | DOPM DEXC |  | OpModIsld DrpV | SPC | GCF | DOPM DEXC.OpModIsld DrpV |  | New
| BO7 | Storage Limit Units. Determines whether the storage Capacity Rating and Storage Reserve are set in units of Amp-hrs or Watt-hrs. If Amp-hrs is selected (the default), AO Capacity Rating and AO Storage Reserve are set using amp-hrs.. If Watt-hrs is selected, AO Capacity Rating and AO Storage Reserve are set using watt-hrs. | X | X | X | X | X | X | X | X | X |  |  | Amp-hrs (default) | Watt-hrs | 2 | 2 | DRCT |  | AGra |  | INV4 | DRCT.AGra |  | New
| BO8 | Power factor excitation (operating quadrant) Here for IEC 61850 compatibility, not implemented | X | X | X | X | X | X | X | X | X |  |  | Producing VARs - Q1/Q2 | Absorbing VARs - Q3/Q4 | 2 | 2 | DRCT |  | PFExt | SPG | INV3 | DRCT.PFExt | Yes | New | Move to system
| BO9 | Enable Low/High Voltage Ride-Through Mode | X | X | X | X | X | X | X | X | X |  |  | Disabled | Enabled | 2 | 2 | DVRT |  | Mod | SPC |  | DVRT.Mod | Yes
| BO10 | Enable Low/High Frequency Ride-Through Mode | X | X | X | X | X | X | X | X | X |  |  | Disabled | Enabled | 2 | 2 | DFRT |  | Mod | SPC |  | DFRT.Mod | Yes
| BO11 | Enable Dynamic Reactive Current Support Mode | X | X | X | X | X | X | X | X | X |  |  | Disabled | Enabled | 2 | 2 | RDGS |  | Mod | SPC | TV31 | RDGS.Mod | Yes | New, name is per MESA word document
| BO12 | Enable Dynamic Volt-Watt Mode | X | X | X | DCTE | X | X | X | X | X |  |  | Disabled | Enabled |  |  | DVWD |  | Mod | SPC |  | DVWD.Mod | Yes | New, added per #item 60
| BO13 | Enable Frequency-Watt Emergency Mode | X | X | X | X | X | X | X | X | X |  |  | Disabled | Enabled | 2 | 2 | FWHZ |  | Mod | SPC |  | FWHZ.Mod | Yes
| BO14 | Enable Active Power Limit Mode | X | X | X | X | X | X | X | X | X |  |  | Disabled | Enabled | 2 | 2 | DAMG |  | Mod | SPC | INV2 | DAMG.Mod | Yes | New IEC 61850 name to match 7-420 | Active Power Limit is Active Power Limit Discharging or Discharging in MESA spec document. Was also called limited watts in old DNP3 data points
| BO15 | Enable Charge/Discharge Mode | X | X | X | X | X | X | X | X | X |  |  | Disabled | Enabled | 2 | 2 | DCHA |  | Mod | SPC | INV4 | DCHA.Mod | Yes | New IEC 61850 name to match 7-420 | Mode of operation - charge or discharge rate
| BO16 | Enable Coordinated Charge/Discharge Mode | X | X | X | X | X | X | X | X | X |  |  | Disabled | Enabled | 2 | 2 | DCBY |  | Mod | SPC |  | DCBY.Mod | Yes | New
| BO17 | Enable Peak Power Limiting Mode | X | X | X | X | X | X | X | X | X |  |  | Disabled | Enabled | 2 | 2 | DLFL |  | Mod | SPC | PPL | DLFL.Mod | Yes | New | Was Mode of Operation - Peak Power (Load) Limiting in older DNP3 points list
| BO18 | Enable Load Following Mode | X | X | X | X | X | X | X | X | X |  |  | Disabled | Enabled | 2 | 2 | DGFL |  | Mod | SPC | LGF | DGFL.Mod | Yes | New | Was Mode of Operation - Load / Generation Following in older DNP3 points list
| BO19 | Enable Generation Following Mode | X | X | X | X | X | X | X | X | X |  |  | Disabled | Enabled | 2 | 2 | DGFL |  | Mod | SPC | LGF | DGFL.Mod | Yes | New | Was Mode of Operation - Load / Generation Following in older DNP3 points list
| BO20 | Enable Automatic Generation Control Mode | X | X | X | X | X | X | X | X | X |  |  | Disabled | Enabled | 2 | 2 | DCHA |  | Mod | SPC |  | DCHA.Mod | Yes | New
| BO21 | Enable Active Power Smoothing Mode | X | X | X | X | X | X | X | X | X |  |  | Disabled | Enabled | 2 | 2 | DWSM |  | Mod | SPC | RPS | DWSM.Mod | Yes | New | Was Mode of operation - Active Power Smoothing in old DNP3 points list
| BO22 | Enable Volt-Watt Mode | X | X | X | X | X | X | X | X | X |  |  | Disabled | Enabled | 2 | 2 | DVWA DVVM |  | Mod | SPC | DVW | DVWA DVVM.Mod | Yes | New
| BO23 | Enable Frequency-Watt Smoothing Mode | X | X | X | X | X | X | X | X | X |  |  | Disabled | Enabled | 2 | 2 | DFWS |  | Mod | SPC |  | DFWS.Mod | Yes | New
| BO24 | Enable Fixed Power Factor Mode | X | X | X | X | X | X | X | DCTE | X |  |  | Disabled | Enabled | 2 | 2 | DFPF |  | Mod | SPC | INV3 | DFPF.Mod | Yes | New IEC 61850 name to match 7-420 | Was Mode of operation - maintaining fixed power factor in older DNP3 point list
| BO25 | Enable Volt-VAR Control Mode | X | X | X | X | X | X | X | DCTE | X |  |  | Disabled | Enabled | 2 | 2 | DVVC |  | Mod | SPC |  | DVVC.Mod | Yes | New
| BO26 | Enable Watt-VAr Mode | X | X | X | X | X | X | X | X | X |  |  | Disabled | Enabled | 2 | 2 | FPFW |  | Mod | SPC |  | FPFW.Mod | Yes | New
| BO27 | Enable Power Factor Correction Mode | X | X | X | X | X | X | X | X | X |  |  | Disabled | Enabled | 2 | 2 | DPFC |  | Mod | SPC |  | DPFC.Mod | Yes | New
| BO28 | Enable Pricing Mode | [11 empty] | Disabled | Enabled | 2 | 2 | DPRG |  | Mod | SPC | INV5 | DPRG.Mod | Yes | New, added per item #58 | Was Mode of operation - pricing signal in old DNP3 points list
| BO29 | Dynamic Reactive Current Mode. Selects the priority of whether or not Watts should be curtailed in order to produce the reactive current required by this function. | [11 empty] | Reactive current is preferred over Watts for grid support | Watts are preferred over reactive current for grid support |  |  | RDGS |  | Mod | ENG |  | RDGS.Mod | Yes | New added per MESA Word document
| BO30 | Dynamic Reactive Current Priority. Selects the priority of whether or not Watts should be curtailed in order to produce the reactive current required by this function. | [11 empty] | Wattts can be curtailed in order to produce reactive current. | Watt should not be curtailed in order to produce reactive current |  |  | FMAR |  | DepRef.2 or .3 | ENG |  | FMAR.DepRef.2 or .3 | Yes | New added per MESA Word document
| BO31 | Curve Enable. Enable the currently selected curve. | X | X | X | X | X | X | X | X | X |  |  | Disable | Enable | 2 | 2 | DGSM | n > 10 | ModEna | SPC | VV11-12 | DGSMn > 10.ModEna | Yes | New
| S (S=35 for this version of the specifcation) | Set Selected Scheduled Ready | X | X | X | X | X | X | X | X | X |  |  | Not Ready | Ready | 2 | 2 | FSCH | xx | Mod | ENC |  | FSCHxx.Mod | Yes
| #REF! | Set Selected Schedule Repeat Weekly Sunday | X | X | X | X | X | X | X | X | X |  |  | Do Not Repeat | Repeat | 2 | 2 | FSCH | xx | SchdReuse | SPG |  | FSCHxx.SchdReuse | Yes
| S+1 | Set Selected Schedule Repeat Weekly Monday | X | X | X | X | X | X | X | X | X |  |  | Do Not Repeat | Repeat | 2 | 2 | FSCH | xx | SchdReuse | SPG |  | FSCHxx.SchdReuse | Yes
| #REF! | Set Selected Schedule Repeat Weekly Tuesday | X | X | X | X | X | X | X | X | X |  |  | Do Not Repeat | Repeat | 2 | 2 | FSCH | xx | SchdReuse | SPG |  | FSCHxx.SchdReuse | Yes
| #REF! | Set Selected Schedule Repeat Weekly Wednesday | X | X | X | X | X | X | X | X | X |  |  | Do Not Repeat | Repeat | 2 | 2 | FSCH | xx | SchdReuse | SPG |  | FSCHxx.SchdReuse | Yes
| S+2 | Set Selected Schedule Repeat Weekly Thursday | X | X | X | X | X | X | X | X | X |  |  | Do Not Repeat | Repeat | 2 | 2 | FSCH | xx | SchdReuse | SPG |  | FSCHxx.SchdReuse | Yes
| S+3 | Set Selected Schedule Repeat Weekly Friday | X | X | X | X | X | X | X | X | X |  |  | Do Not Repeat | Repeat | 2 | 2 | FSCH | xx | SchdReuse | SPG |  | FSCHxx.SchdReuse | Yes
| S+4 | Set Selected Schedule Repeat Weekly Saturday | X | X | X | X | X | X | X | X | X |  |  | Do Not Repeat | Repeat | 2 | 2 | FSCH | xx | SchdReuse | SPG |  | FSCHxx.SchdReuse | Yes

## CTR
Counters
Point Index | Name / Description | Default Class Assigned to Counter Events | Frozen Counter Exists (Yes or No) | Default Class Assigned to Frozen Counter Events | IEC 61850 |  |  |  |  | MESA-ESS
[5 empty] | LN Class | LN Inst | Data Object | CDC | Function |  | Change | Comment
System Counters | [11 empty] | Note meters can be a measurement point
C0 | DER Unit #1 Real energy supplied to grid (Watt-hours) | n/a | Yes | 3 | MMTR | 1 | SupWh | BCR |  | Yes |  | Not described in 90-7
C1 | DER Unit #1 Reactive energy supplied to grid (VAR-hours) | n/a | Yes | 3 | MMTR | 1 | SupVArh | BCR |  | Yes |  | Not described in 90-7
C2 | DER Unit #1 Real energy received (demanded) from grid (Watt-hours) | n/a | Yes | 3 | MMTR | 1 | DmdWh | BCR |  | Yes |  | Not described in 90-7
C3 | DER Unit #1 Reactive energy received (demanded) from grid (VAR-hours) | n/a | Yes | 3 | MMTR | 1 | DmdVArh | BCR |  | Yes |  | Not described in 90-7
. . . | DER Unit #2 . . . DER Unit #e-1 points
ductr(e-1) | DER Unit #e Real energy supplied to grid (Watt-hours) | n/a | Yes | 3 | MMTR | 1 | SupWh | BCR |  | Yes |  | Not described in 90-7 | DCTE
ductr(e-1)+1 | DER Unit #e Reactive energy supplied to grid (VAR-hours) | n/a | Yes | 3 | MMTR | 1 | SupVArh | BCR |  | Yes |  | Not described in 90-7 | DCTE
ductr(e-1)+2 | DER Unit #e Real energy received (demanded) from grid (Watt-hours) | n/a | Yes | 3 | MMTR | 1 | DmdWh | BCR |  | Yes |  | Not described in 90-7
ductr(e-1)+3 | DER Unit #e Reactive energy received (demanded) from grid (VAR-hours) | n/a | Yes | 3 | MMTR | 1 | DmdVArh | BCR |  | Yes |  | Not described in 90-7
Vendor Specific Counters
DCTE
DCTE
DCTE

## AI
Point Index | Name / Description | Default Event Class | Transmitted Value Minimum | Transmitted Value Maximum | Scaling Multiplier | Off-set | Units | Resolution | LN Class | LN Inst | Data Object | CDC | Unique String | Function | MESA-ESS | Change | Comment
#REF! | DER Profile Version Number. Always the number 0.9 for this specification. | [11 empty] | . |  | Yes
AI0 | DER Profile Implementation Level. 1, 2 or 3 to indicate support for Level 1, Level 2 or Level 3 respectively. |  | 1 | 3 | 1 | 0 | N/A | 1 |  |  |  |  | . |  | Yes
#REF! | Nameplate Voltage Rating – Volts |  | 0 | 2147483647 | 1 | 0 | Volts |  | DRAT |  | VRtg | ASG | DRAT.VRtg |  | Yes
#REF! | Nameplate Active Power Rating – Watts |  | 0 | 2147483647 | 1 | 0 | Watts |  | DRAT |  | WRtg | ASG | DRAT.WRtg |  | Yes
AI1 | Nameplate Apparent Power Rating - VA |  | 0 | 2147483647 | 1 | 0 | VA |  | DRAT |  | VARtg | ASG | DRAT.VARtg |  | Yes
AI2 | Nameplate Reactive Power Rating – VAR |  | 0 | 2147483647 | 1 | 0 | Var |  | DRAT |  | VarRtg | ASG | DCTE |  | Yes
AI3 | Number of System Schedules | 2 | 0 | Varies. May not be r/w | 1 | 0 | None | 1 |  |  |  |  | DCTE |  | Yes
AI4 | Number of Meters | 2 | 0 | Varies. May not be r/w | 1 | 0 | None | 1 | [6 empty] | Yes
AI5 | Number of Inverters | 2 | 0 | Varies. May not be r/w | 1 | 0 | None | 1 | [6 empty] | Yes
AI6 | Number of Batteries | 2 | 0 | Varies. May not be r/w | 1 | 0 | None | 1 | [6 empty] | Yes
AI7 | Number of DER units connected to controller | 2 | 0 | Varies. May not be r/w | 1 | 0 | None | 1 | DRCT |  | DERNum | ING | DRCT.DERNum |  | Yes |  | Per item 70. See 420 for the definition of DERNum: “number of DER units connected to an ECP”.
AI8 | Reference Voltage |  | 0 | 2147483647 | 1 | 0 | Volts | 0.01 | DRCT |  | VRef | ASG | DRCT.VRef |  | Yes
AI9 | Reference Voltage Offset |  | 0 | 2147483647 | 1 | 0 | Volts | 0.01 | DRCT |  | VRefOfs | ASG | DRCT.VRefOfs |  | Yes
AI10 | Maximum Generation Rate |  | 0 | 2147483647 | 1 | 0 | Watts | (1%)% | DRCT |  | WMax | ASG | DRCT.WMax |  | Yes
AI11 | Maximum Charge Rate | 2 | 0 | 2147483647 | 1 | 0 | Watts | (1%) | DRCT |  | WChaMax | ASG | DRCT.WChaMax | INV4 | Yes
AI12 | Maximum Reactive Power |  | 0 | 2147483647 | DCTE | 0 | VARs | (1%) | DRCT |  | VArMax | ASG | DRCT.VArMax |  | Yes
AI13 | Maximum Apparent Generation Power | 2 | 0 | 2147483647 | 1 | 0 | VA | (1%) | DRCT |  | VAMax | ASG | DRCT.VAMax | INV4 | Yes
AI14 | Maximum Apparent Charging Power | 2 | 0 | 2147483647 | 1 | 0 | VA | (1%) | DRCT |  | VAChaMax | ASG | DRCT.VAChaMax | INV4 | Yes | new
AI15 | Minimum Voltage | 2 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | DRCT |  | VMin | ASG | DRCT.VMin | VV11-14 | Yes | new | Not clear how it is used - left as being readable but not writeable
AI16 | Maximum Voltage | 2 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | DRCT |  | Vmax | ASG | DRCT.Vmax | VV11-14 | Yes | new | Not clear how it is used - left as being readable but not writeable
AI17 | Reference for Reactive Power Setpoints. Selects which setpoint is active. Default is <3>. Also specifies whether Watts or VARs take precedence when providing reactive current support. If set to <3>, generating Watts has precedence. At any other setting, reactive current has precedence. <0> Not applicable / Unknown <1> Percent of Maximum Active Power (DRCT.WMax) <2> Percent of Maximum Reactive Power (DRCT.VArMax) <3> Percent of Available Reactive Power (DINV.VArAvl) | 2 | 0 | 3 | 1 | 0 | n/a | 1 | DRCT |  | VArRef | ENG | DRCT.VArRef | VV13-14, TV31 |  | new
AI18 | System Available Apparent Power (in kVAs) | 1 | -2147483648 | 2147483647 | 1 | 0 | kVA | 1 | MMXU |  | TotVA | MV | MMXU.TotVA |  | Yes |  | Added from MESA spec
AI19 | System Start-up Status | 1 | -1 | 99 | 1 | 0 | N/A | 1 |  |  |  |  | . |  | Yes |  | See item #203
AI20 | State of Charge – Currently available energy in the ESS, as a percentage of ACTUAL capacity rating. | 1 | 0 | 1000 | 0.1 | 0 | Percent | 0.1 | DBAT |  | SocWhPct | MV | DBAT.SocWhPct |  | Yes | Added ESS SOC | Per item #99 Suggest keeping all DBAT together
AI21 | Usable State of Charge – Currently usable energy in the ESS, as a percentage of USABLE capacity rating. | [5 empty] | Percent | 0.1 | DBAT |  | SocUsePct | MV | DBAT.SocUsePct |  | Yes | Added ESS SOC | Per item #99 Suggest keeping all DBAT together
AI22 | DER Start Time Window | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DRCC |  | StrWinTms | ING | DRCC.StrWinTms | INV1 | Yes |  | Per item 65 - associated with DERStr in BO
AI23 | DER Start Ramp Up Rate The rate (percent of WMax) used by the system to achieve its generation/discharging setpoints after being soft started. This time overrides the WGra generation ramp rate for startup. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DRCC |  | StrRmpUpRte | ING | DRCC.StrRmpUpRte | INV1 | Yes | New | Per item 65, and item 70
AI24 | DER Stop (Cease to Energize) Time Window | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DCTE |  | StopWinTms | ING | DCTE.StopWinTms | INV1 | Yes |  | Per item 65 associated with DERStop in BO
AI25 | DER Stop (Cease to Energize) Ramp Down Rate | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DCTE |  | StopRmpDnRte | ING | DCTE.StopRmpDnRte | INV1 | Yes | New | Per item 65, and item 70
AI26 | Connect/Disconnect Time Window | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 |  |  | WinTms | ING | .WinTms | INV1 | Yes |  | Per item 65 - Suggest deleting - don't need both
AI27 | Connect/Disconnect Reversion Timeout Period . Timeout (reversion time is for the Disconnect only) | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 |  |  | RvrtTms | ING | .RvrtTms | INV1 | Yes |  | Per item 65 - Suggest deleting - don't need both
AI28 | Setpoint for Nominal Frequency | 2 | 0 | 70000 | 0.001 | 0 | Hz | 1 | DOPR |  | ECPNomHz | ASG | DOPR.ECPNomHz | FW22 | Yes | Frequency scaling is .001 Hz per item #69
AI29 | Generation Ramp Up Rate. Percentage of Maximum Generation Rate (WMax) that the generation rate can change per minute when ramping up. |  | 0 | 1000 | 0.1 | 0 | Percent per min | 1 | DRCT |  | RmpUpRte | ING | DRCT.RmpUpRte |  | Yes
AI30 | Generation Ramp Down Rate. Percentage of Maximum Generation Rate (Wmax) that the generation rate can change per minute when ramping down. |  | 0 | 1000 | 0.1 | 0 | Percent per min | 1 | DRCT |  | RmpDnRte | ING | DRCT.RmpDnRte |  | Yes
AI31 | Maximum Generation Ramp Up Rate. The maximum generation ramp up rate expressed as a percentage of the Maximum Generation Rate (Wcha) per minute. |  | 0 | 1000 | 0.1 | 0 | Percent per min | 1 | DRCT |  | RmpUpRteMax | ING | DRCT.RmpUpRteMax |  | Yes
AI32 | Maximum Generation Ramp Down Rate. The maximum generation ramp down rate expressed as a percentage of the Maximum Generation Rate (Wcha) per minute. |  | 0 | 1000 | 0.1 | 0 | Percent per min | 1 | DRCT |  | RmpDnRteMax | ING | DRCT.RmpDnRteMax |  | Yes
AI33 | Charging Ramp Up Rate. Percentage of Maximum Charging Rate (WChaMax) that the charging rate can change per minute when ramping up. |  | 0 | 1000 | 0.1 | 0 | Percent per min | 1 | DRCT |  | RmpUpRteCha | ING | DRCT.RmpUpRteCha |  | Yes
AI34 | Charging Ramp Down Rate. Percentage of Maximum Charging Rate (WChaMax) that the charging rate can change per minute when ramping down. |  | 0 | 1000 | 0.1 | 0 | Percent per min | 1 | DRCT |  | RmpDnRteCha | ING | DRCT.RmpDnRteCha |  | Yes
AI35 | Maximum Charging Ramp Up Rate. The maximum charging ramp up rate expressed as a percentage of the Maximum Charging Rate (WChaMax) per minute. | 2 | 0 | 1000 | 0.1 | 0 | Percent per min | 1 | DBAT |  | RmpUpRteChaMax | ING | DBAT.RmpUpRteChaMax |  | Yes |  | these are storage-related values, which are separate from the charge/discharge function. They should be treated the same way as the PV, CHP, etc
AI36 | Maximum Charging Ramp Down Rate. The maximum charging ramp down rate expressed as a percentage of the Maximum Charnging Rate (WChaMax) per minute. | 2 | 0 | 1000 | 0.1 | 0 | Percent per min | 1 | DBAT |  | RmpDnRteChaMax | ING | DBAT.RmpDnRteChaMax |  | Yes
AI37 | Storage Actual Capacity. Actual total watt capacity of the storage system | [5 empty] | Amp-hours |  | DBAT |  | WhrRtg |  | DBAT.WhrRtg |  | Yes |  | these are storage-related values, which are separate from the charge/discharge function. They should be treated the same way as the PV, CHP, etc
AI38 | Storage Usable Capacity. Usable watt capacity of the storage system for this function | [5 empty] | Watts |  | DBAT |  | CapWhrUse |  | DBAT.CapWhrUse |  | Yes |  | these are storage-related values, which are separate from the charge/discharge function. They should be treated the same way as the PV, CHP, etc
AI39 | Requested Settings Group <0> Not Used <1> Unspecified / Autonomously Determined (see BO Enable Sensed Grid Config Detection) <2> Factory Configuration <3> Default Configuration / Comms Lost <4> Normal Grid-Connected Configuration <5> Islanded Condition 1 (small, local island) <6> Islanded Condition 2 (larger, area island) <7> Islanded Condition 3 (largest, regional island) <8> 1st Alternate Grid-Connected Configuration <9> 2nd Alternate Grid-Connected Configuration <10> 3rd Alternate Grid-Connected Configuration <11-255> Reserved for future assignment | 2 | 0 | 10 | 1 | 0 | n/a | 1 | DRCC |  | GridCfgSel | ENG | DRCC.GridCfgSel | GCF |  | new | Proposed by EPRI? But not yet thought about in 61850
AI40 | Settings Group Being Edited <0> Not Used <1> Unspecified / Autonomously Determined (see BO Enable Sensed Grid Config Detection) <2> Factory Configuration <3> Default Configuration / Comms Lost <4> Normal Grid-Connected Configuration <5> Islanded Condition 1 (small, local island) <6> Islanded Condition 2 (larger, area island) <7> Islanded Condition 3 (largest, regional island) <8> 1st Alternate Grid-Connected Configuration <9> 2nd Alternate Grid-Connected Configuration <10> 3rd Alternate Grid-Connected Configuration <11-255> Reserved for future assignment | 2 | 0 | 10 | 1 | 0 | n/a | 1 | DRCC |  | GridCfgEdt | ENG | DRCC.GridCfgEdt | GCF |  | new | Proposed by EPRI? But not yet thought about in 61850
AI41 | Active Settings Group. Note this may differ from the Requested Settings Group or Settings Group Being Edited analog outputs depending on whether communications has been lost and how the Enable Sensed Grid Config Detection binary output is set. <0> Not Used <1> Unspecified / Autonomously Determined (see BO42) <2> Factory Configuration <3> Default Configuration / Comms Lost <4> Normal Grid-Connected Configuration <5> Islanded Condition 1 (small, local island) <6> Islanded Condition 2 (larger, area island) <7> Islanded Condition 3 (largest, regional island) <8> 1st Alternate Grid-Connected Configuration <9> 2nd Alternate Grid-Connected Configuration <10> 3rd Alternate Grid-Connected Configuration <11-255> Reserved for future assignment | 2 | 0 | 255 | 1 | 0 | n/a | 1 | DRCS |  | GridCfgSt | ENS | DRCS.GridCfgSt | GCF |  | new | Proposed by EPRI? But not yet thought about in 61850
AI42 | Freeze Counter Interval. interval between freeze counter operations after the initial occurrence. A zero value means the free counter operation is not repeated. | 2 | 0 | 2147483647 | 1 | 0 | N/A | 1 |  |  |  |  | . |  |  |  | Replaces "Freeze at Time" in DNP3
AI43 | Freeze Counter Interval Units. Units of the interval between freeze counter operations: <0> The outstation does not repeat the action, regardless of the Interval count. <1> Milliseconds - In this case the interval is always counted relative to the Start Time and is constant regardless of the clock time set at the Outstation. <2> Seconds - At the same millisecond within the second that is specified in the Start Time. <3> Minutes - At the same second and millisecond within the minute that is specified in the Start Time. <4> Hours - At the same minute, second and B7millisecond within the hour that is specified in the Start Time. <5> Days - At the same time of day that is specified in the Start Time. <6> Weeks - On the same day of the week at the same time of day that is specified in the Start Time <7> Months - On the same day of each month at the same time of day that is specified in the Start Time. If the Start Time falls on the 29th or greater day of the month, the outstation shall not perform the action in months that do not have such a day <8> Months on Same Day of Week from Start of Month - At the same timeof day on the same day of the week after the beginning of the month as the day specified in the Start Time. For instance, if the Start Time specifies the second Tuesday of February and the Interval Count is 2, the next action shall occur on the second Tuesday of April. In the same example, if the Interval Count is set to 12, this is the same as specifying, “Every year on the second Tuesday in February”. If the specified day does not occur in a given month when an action was scheduled to occur, the outstation shall not perform the action that month but shall perform it at the next valid scheduled time. <9> Months on Same Day of Week from End of Month - The outstation shall interpret this setting as in <8>, but the day of the week shall be measured from the end of the month, e.g.,“the second-last Tuesday in February”. | 2 |  | 9 | 1 | 0 | N/A | 1 |  |  |  |  | . |  |  |  | Replaces "Freeze at Time" in DNP3
AI44 | Low/High Voltage Ride-Through Signal Meter ID. Referenced ECP. This is the meter from which current is being read to evaluate and provide support. | [7 empty] | DVRT |  | ECPRefId |  |  |  | Yes
AI45 | Low/High Voltage Ride-Through Voltage Reference Input. Active Power measurement read from the meter and used as an input to the mode. | [7 empty] | DVRT |  | VolRef |  |  |  | Yes
AI46 | Low/High Voltage Ride-Through High Must Trip Curve Index. Index of the Voltage Ride-through curve which specifies trip points when the voltage is high. | [13 empty] | Yes
AI47 | Low/High Voltage Ride-Through Low Must Trip Curve Index. Index of the Voltage Ride-through curve which specifies trip points when the voltage is low. | [13 empty] | Yes
AI48 | Low/High Frequency Ride-Through Signal Meter ID. Referenced ECP. This is the meter from which current is being read to evaluate and provide support. | [13 empty] | Yes
AI49 | Low/High Frequency Ride-Through Voltage Reference Input. Active Power measurement read from the meter and used as an input to the mode. | [13 empty] | Yes
AI50 | Low/High Frequency Ride-Through High Must Trip Curve Index. Index of the Frequency Ride-through curve which specifies trip points when the frequency is high. | [13 empty] | Yes
AI51 | Low/High Frequency Ride-Through Low Must Trip Curve Index. Index of the Frequency Ride-through curve which specifies trip points when the frequency is low. | [13 empty] | Yes
AI52 | Dynamic Reactive Current Support - Meter ID: Referenced ECP. This is the meter from which current is being read to evaluate and provide support. | 2 | 0 | 2147483647 | 1 | 0 | n/a | 1 | RDGS |  | ECPRefId | ING | RDGS.ECPRefId | TV31 | Yes |  | Referenced ECP - does not yet exist in 61850
AI53 | Dynamic Reactive Current Support - Gradient Mode: <0> Undefined <1> Gradients reach 0 at the moving average Voltage <2> Gradients reach 0 at the Voltage deadbands | 2 | 0 | 2 | 1 | 0 | n/a | 1 | RDGS |  | ArGraMod | ENG | RDGS.ArGraMod | TV31 | Yes | New, listed as "To Do" item in MESA set of points
AI54 | Dynamic Reactive Current Support Deadband Minimum Voltage. Percentage of the nominal voltage (DRCT.Vref), measured from the moving average voltage (RDGS.VAv). Support is no longer applied when the voltage stays above this value for the length of the Hold Time. | 2 | 0 | 1000 | 0.1 | 0 | Percent | 1 | RDGS |  | DbVMin | ASG | RDGS.DbVMin | TV31 | Yes
AI55 | Dynamic Reactive Current Support Deadband Maximum Voltage when applying reactive current support. Percentage of the nominal voltage (DRCT.Vref), measured from the moving average voltage (RDGS.VAv). Support is no longer applied when the voltage stays below this value for the length of the Hold Time. | 2 | 0 | 1000 | 0.1 | 0 | Percent | 1 | RDGS |  | DbVMax | ASG | RDGS.DbVMax | TV31 | Yes
AI56 | Dynamic Reactive Current Support Gradient for Sags. This is the percentage of the rated current (DRAT.ARtg) to apply capacitively per percentage of the negative deviation from the moving average voltage (RDGS.Av). It is a ratio of percent and is therefore unitless. | 2 | -2147483648 | 2147483647 | 0.001 | 0 | n/a | 1 | RDGS |  | ArGraSag | ASG | RDGS.ArGraSag | TV31 | Yes
AI57 | Dynamic Reactive Current Support Gradient for Swells . Percentage of the rated current (DRAT.ARtg) to apply inductively per percentage of the positive deviation from the moving average voltage (RDGS.Av). It is a ratio of percent and is therefore unitless. | 2 | -2147483648 | 2147483647 | 0.001 | 0 | n/a | 1 | RDGS |  | ArGraSwell | ASG | RDGS.ArGraSwell | TV31 | Yes
AI58 | Dynamic Reactive Current Support Filter Time for Moving Average Voltage (RDGS.VAv) used to determine amount of dynamic reactive current support | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | RDGS |  | FiltTms | ING | RDGS.FiltTms | TV31 | Yes
AI59 | Dynamic Reactive Current Support Block Zone Voltage.Percentage of the nominal voltage (DRCT.VRef) below which no reactive current support shall be applied. | 2 | 0 | 1000 | 0.1 | 0 | Percent | 1 | RDGS |  | BlkZnV | ASG | RDGS.BlkZnV | TV31 | Yes
AI60 | Dynamic Reactive Current Support Hysteresis Block Zone Voltage for applying dynamic reactive current support. This is a percentage of the nominal voltage (DRCT.VRef). After being blocked, reactive current support shall not resume until the voltage has been above BlkZnV + HysBlkZnV. | 2 | 0 | 1000 | 0.1 | 0 | Percent | 1 | RDGS |  | HysBlkZnV | ASG | RDGS.HysBlkZnV | TV31 | Yes
AI61 | Dynamic Reactive Current Support Block Zone Time. Time in milliseconds from the beginning of any "sag" event, before which dynamic reactive current support will always continue, regardless of how low voltage may sag. | 2 | 0 | 2147483647 | 1 | 0 | ms | 1 | RDGS |  | BlkZnTmms | ING | RDGS.BlkZnTmms | TV31 | Yes
AI62 | Dynamic Reactive Current Support Hold Time. When the voltage returns to within the deadband limits (RDGS.dbVMin annd RDGS.dbVMax) for this length of time (measured in milliseconds), the "sag" or "swell" event is considered to be over. Reactive current support ends, frozen values are unfrozen, and a new event can begin. | 2 | 0 | 2147483647 | 1 | 0 | ms | 1 | RDGS |  | HoldTmms | ING | RDGS.HoldTmms | TV31 | Yes
AI63 | Dynamic Reactive Current Support Moving Average Voltage | 2 | 0 | 2147483647 | 1 | 0 | Volts | 1 | RDGS |  | Vav | MV | RDGS.Vav | TV31 | Yes | new | Calculated
AI64 | Dynamic Reactive Current Support Present Delta Voltage. Difference in Volts between the present measured Voltage and the Moving Average Voltage (RDGS.Vav) as a percentage of the reference voltage (VRef) | 2 | 0 | 1000 | 0.1 | 0 | Percent | 1 | RDGS |  | DelV | MV | RDGS.DelV | TV31 | Yes | new | Calculated
AI65 | Dynamic Reactive Current Support Mode Priority |  | 0 | number of modes | 1 | 0 | n/a | 1 | RDGS |  | ModPrty | ING | RDGS.ModPrty |  | Yes
AI66 | Dynamic Volt-Watt Gradient. Signed unit-less quantity that establishes the ratio of additional Watts supplied (expressed in terms of % DRCT.WMax) to the present difference from the moving average voltage (expressed as % DRCT.VRef). | 2 | -2147483648 | 2147483647 | 0.001 | 0 | n/a | 1 | DVWD |  | DynVWGra | ASG | DVWD .DynVWGra | VW52 | Yes
AI67 | Dynamic Volt-Watt Filter Time. The time in seconds used to calculate the moving average voltage for dynamic Volt-Watt support. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DVWD |  | VWFilTms | ASG | DVWD .VWFilTms |  | Yes
AI68 | Dynamic Volt-Watt Lower Deadband. Percentage of the nominal voltage (DRCT.Vref) measured below the moving average voltage. If the present voltage is above this value, no additional Watts shall be supplied. | 2 | 0 | 1000 | 0.1 | 0 | Volts | 1 | DVWD |  | DbVWLo | ASG | DVWD .DbVWLo |  | Yes
AI69 | Dynamic Volt-Watt Upper Deadband. Percentage of the nominal voltage (DRCT.Vref) measured above the moving average voltage. If the present voltage is below this value, no additional Watts shall be supplied. | 2 | 0 | 1000 | 0.1 | 0 | Volts | 1 | DVWD |  | DbVWHi | ASG | DVWD .DbVWHi |  | Yes
AI70 | Dynamic Volt-Watt Reversion Timeout Period | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DVWD |  | RevtTms | ING | DVWD .RevtTms |  | Yes
AI71 | Dynamic Volt-Watt Mode Priority |  | 0 | number of modes | 1 | 0 | n/a | 1 | DVWD |  | ModPrty | ING | DVWD .ModPrty |  | Yes
AI72 | Frequency-Watt Emergency Signal Meter ID | [7 empty] | FWHZ | 2 | ECPRefId | ASG | FWHZ2.ECPRefId | FW1 | Yes
AI73 | Frequency-Watt Emergency Frequency Reference Input. Frequencye measurement read from the meter and used as an input to the mode. | [7 empty] | FWHZ | 2 | HzRef | MV | FWHZ2.HzRef |  | Yes
AI74 | Frequency-Watt Emergency High speed enable/disable: Activation of the Active Power Reduction by Frequency function ctlVal = off (FALSE) ¦ on (TRUE) | [7 empty] | FWHZ | 2 | WCtlHzEna | ASG | FWHZ2.WCtlHzEna |  | Yes
AI75 | Frequency-Watt Emergency Starting frequency: Delta frequency between start frequency and nominal grid frequency | [7 empty] | FWHZ | 2 | HzStr | ASG | FWHZ2.HzStr |  | Yes
AI76 | Frequency-Watt Emergency Stopping frequency: Delta frequency between stop frequency and nominal grid frequency | [7 empty] | FWHZ | 2 | HzStop | ASG | FWHZ2.HzStop |  | Yes
AI77 | Frequency-Watt Emergency Maximim W change rate: The maximum rate at which the ouput may be increased after releasing the frozen value of snap shot function. This is represented in terms of % WMax per minute. | [7 empty] | FWHZ | 2 | HzStopWGra | ASG | FWHZ2.HzStopWGra |  | Yes
AI78 | Frequency-Watt Emergency Activation delay: Intentional delay in ms before function activation | [5 empty] | ms |  | FWHZ | 2 | ActDlTmms | ING | FWHZ2.ActDlTmms |  | Yes
AI79 | Frequency-Watt Emergency Hysteresis enable/disable True = Use of hysteresis; False = No use of hysteresis | [7 empty] | FWHZ | 2 | HysEna | SPG | FWHZ2.HysEna |  | Yes
AI80 | Frequency-Watt Emergency Snapshot of power: True = Snapshot is active; False = Off, the snapshot is not active | [7 empty] | FWHZ | 2 | SnptW | SPG | FWHZ2.SnptW |  | Yes
AI81 | Frequency-Watt Emergency Mode Priority |  | 0 | number of modes | 1 | 0 | n/a | 1 | FWHZ | 2 | ModPrty | ING | FWHZ2.ModPrty |  | Yes
AI82 | Active Power Limit Signal Meter ID | [7 empty] | DAMG |  | ECPRefId | ORG | DAMG.ECPRefId | INV2 | Yes
AI83 | Active Power Limit Reference Input. Active Power measurement read from the meter and used as an input to the mode. | [5 empty] | Watts |  | DAMG |  | WRef | MV | DAMG.WRef |  | Yes
AI84 | Active Power Limit Charge Setpoint. Limit of imported Watts as a percentage of Maximum Active Power capability, | 2 | 0 | 1000 | 0.1 | 0 | Percent | 0.1 | DAMG |  | WImpLimPct | ING | DAMG.WImpLimPct |  | Yes | New | Per item 67
AI85 | Active Power Limit Discharge Setpoint. Limit of exported Watts as a percentage of Maximum Active Power capability, | 2 | 0 | 1000 | 0.1 | 0 | Percent | 1 | DAMG |  | WExpLimPct | ING | DAMG.WExpLimPct |  | Yes | New | Per item 67
AI86 | Active Power Limit Time Window. Time window (in seconds) within which to randomly execute a command. If the time window is zero, the command will be executed immediately | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DAMG |  | WinTms | ING | DAMG.WinTms |  | Yes
AI87 | Active Power Limit Reversion Timeout Period. Reversion Timeout Period (in seconds), after which the device will revert to its default status, such as closing the switch to reconnect to the grid or allowing maximum watts output, in case communications are lost or mitigating messages are not received | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DAMG |  | RvrtTms | ING | DAMG.RvrtTms |  | Yes
AI88 | Active Power Limit Ramp Time. Ramp time, in seconds, for moving from current operational mode settings to new operational mode settings | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DAMG |  | RmpTms | ING | DAMG.RmpTms |  | Yes
AI89 | Active Power Limit Mode Priority |  | 0 | number of modes | 1 | 0 | n/a | 1 | DAMG |  | ModPrty | ING | DAMG.ModPrty |  | Yes |  | Not yet in 61850
AI90 | Charge/Discharge Active Power Target | 2 | [6 empty] | DCHD |  | WTgt | ASG | DCHD.WTgt | INV4 | Yes
AI91 | Charge/Discharge Time Window | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DCHD |  | WinTms | ING | DCHD.WinTms |  | Yes
AI92 | Charge/Discharge Ramp Time. Ramp time, in seconds, for moving from current operational mode settings to new operational mode settings | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DCHD |  | RmpTms | ING | DCHD.RmpTms |  | Yes
AI93 | Charge/Discharge Reversion Timeout Period | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DCHD |  | RevtTms | ING | DCHD.RevtTms |  | Yes
AI94 | Charge/Discharge Discharge Ramp Up Rate | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DCHD |  | RmpUpRte | ING | DCHD.RmpUpRte |  | Yes
AI95 | Charge/Discharge Discharge Ramp Down Rate | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DCHD |  | RmpDnRte | ING | DCHD.RmpDnRte |  | Yes
AI96 | Charge/Discharge Charge Ramp Up Rate | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DCHD |  | ChaRmpUpRte | ING | DCHD.ChaRmpUpRte |  | Yes
AI97 | Charge/Discharge Charge Ramp Down Rate | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DCHD |  | ChaRmpDnRte | ING | DCHD.ChaRmpDnRte |  | Yes
AI98 | Charge/Discharge VAr Action. Action to take when switching between charging and discharging: <0> Reserved <1> Reverse producing/absorbing Vars when changing between charging and discharging (go to diagonal quadrant Q1/Q3 or Q2/Q4) <2> Do not reverse producing/absorbing Vars (go to adjacent quadrant Q1/Q2 or Q3/Q4) | 2 | 0 | 2 | 1 | 0 | n/a | 1 | DCHD |  | VArAct | ENG | DCHD.VArAct |  | Yes | In the basic profile <1> was the only value permitted. | Default is <1>.
AI99 | Charge/Discharge Mode Priority | [7 empty] | DCHD |  | ModPrty | ING | DCHD.ModPrty |  | Yes
AI100 | Charge/Discharge Minimum Reserve for Storage. The reserve level below which the storage system may be only be discharged in emergency situations, expressed as a percentage of the usable capacity. | 2 | -1000 | 1000 | 1 | 0 | Percent | 0.1 | DBAT |  | UseCapMin |  | DBAT.UseCapMin |  | Yes |  | these are storage-related values, which are separate from the charge/discharge function. They should be treated the same way as the PV, CHP, etc
AI101 | Charge/Discharge Maximum Reserve for Storage. The reserve level above which the storage system may be only be charged in emergency situations, expressed as a percentage of the usable capacity. | 2 | -1000 | 1000 | 1 | 0 | Percent | 0.1 | DBAT |  | UseCapMax |  | DBAT.UseCapMax |  | Yes |  | these are storage-related values, which are separate from the charge/discharge function. They should be treated the same way as the PV, CHP, etc
AI102 | Coordinated Charge/Discharge Time Window | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DTCD |  | WinTms | ING | DTCD.WinTms |  | Yes
AI103 | Coordinated Charge/Discharge Ramp Time. Ramp time, in seconds, for moving from current operational mode settings to new operational mode settings | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DTCD |  | RmpTms | ING | DTCD.RmpTms |  | Yes
AI104 | Coordinated Charge/Discharge Reversion Timeout Period | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DTCD |  | RevtTms | ING | DTCD.RevtTms |  | Yes
AI105 | Coordinated Charge/Discharge Target State of Charge. Charge that the system is expected to achieve, as a percentage of the usable capacity. | 2 | 0 | 1000 | 0.1 | 0 | Percent | 0.1 | DTCD |  | SOCUseTgt | ING | DTCD.SOCUseTgt | Charge-By | Yes
AI106 | Coordinated Charge/Discharge Target Date. Date by which the storage system must reach the target SOC. Days since Jan 1, 1970. | 2 | 0 | 2147483647 | 1 | 0 | Seconds |  | DTCD |  | DateTgt | ING | DTCD.DateTgt |  | Yes
AI107 | Coordinated Charge/Discharge Target Time. Time by when the storage system must reach the target SOC. Seconds since midnight. | 2 | 0 | 2147483647 | 1 | 0 | Seconds |  | DTCD |  | DateTgtTms | ING | DTCD.DateTgtTms |  | Yes
AI108 | Coordinated Charge/Discharge Energy Request. Amount of energy that must be transferred from the grid to the charger to move the SOC from the value at the specific time of reference to the target SOC. | 2 | 0 | 2147483647 | 1 | 0 | Watt-hours |  | DTCD |  | SOCW | ING | DTCD.SOCW |  | Yes | Added from EPRI Common Inverter Functions forCoordinated Charge/Discharge function.
AI109 | Coordinated Charge/Discharge Minimum Charging Duration. Minimum duration to move from the SOC at the time of reference to the target SOC. | 2 | 0 | 2147483647 | 1 | 0 | Seconds |  | DTCD |  | ChaDurTms | ING | DTCD.ChaDurTms |  | Yes | Added from EPRI Common Inverter Functions for Coordinated Charge/Discharge function.
AI110 | Coordinated Charge/Discharge Time of Reference. Time that the SOC is measured or computed by the storage system and is the basis for the Energy Request, Minimum Charging Duration, and other parameters | 2 | 0 | 2147483647 | 1 | 0 | Seconds |  | DTCD |  | SOCChaTmsRef | ING | DTCD.SOCChaTmsRef |  | Yes | Added from EPRI Common Inverter Functions forCoordinated Charge/Discharge function.
AI111 | Coordinated Charge/Discharge Duration at Maximum Charge Rate. Duration that energy can be stored at the Maximum Charge Rate. | 2 | 0 | 2147483647 | 1 | 0 | Seconds |  | DTCD |  | SOCChaDurMax | ING | DTCD.SOCChaDurMax |  | Yes | Added from EPRI Common Inverter Functions forCoordinated Charge/Discharge function.
AI112 | Coordinated Charge/Discharge Duration Maximum Discharge Rate. Duration that energy can be delivered at the Maximum Discharge Rate. | 2 | 0 | 2147483647 | 1 | 0 | Seconds |  | DTCD |  | SOCChaDurMin | ING | DTCD.SOCChaDurMin |  | Yes | Added from EPRI Common Inverter Functions forCoordinated Charge/Discharge function.
AI113 | Coordinated Charge/Discharge Mode Priority |  | 0 | number of modes | 1 | 0 | n/a | 1 | DTCD |  | ModPrty | ING | DTCD.ModPrty |  | Yes
AI114 | Peak Power Limiting Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 | n/a | 1 | DPKP |  | ECPRefId | ORG | DPKP.ECPRefId | PPL | Yes |  | Still struggling with the differences between these 3 functions. It may be best to keep them as separate at the moment
AI115 | Peak Power Limiting Reference Power Measured | 2 | 0 | 2147483647 | 1 | 0 | Watts | 1 | DPKP |  | PkPwrWRef | MV | DPKP.PkPwrWRef |  | Yes
AI116 | Peak Power Limit. This is the target value of the reference load power in watts. The DER shall generate Watts to ensure the reference load does not exceed this limit. | 2 | 0 | 2147483647 | 1 | 0 | Watts | 1 | DPKP |  | PkPwrWLim | ASG | DPKP.PkPwrWLim |  | Yes
AI117 | Peak Power Limiting Ratio. If 100%, then peak power is limited to the limit value. If < 100%, then peak power is limited to the remaining percentage over the limit. | [7 empty] | DPKP |  | PkPwrFolPct | ING | DPKP.PkPwrFolPct |  | Yes
AI118 | Peak Power Limiting Time Window | 2 | 0 | 2147483647 | 1 | 0 | Sec | 1 | DPKP |  | WinTms | ING | DPKP.WinTms |  | Yes
AI119 | Peak Power Limiting Reversion Timeout Period | 2 | 0 | 2147483647 | 1 | 0 | Sec | 1 | DPKP |  | RevtTms | ING | DPKP.RevtTms |  | Yes
AI120 | Peak Power Limiting Ramp Time | [7 empty] | DPKP |  | RmpTms | ING | DPKP.RmpTms |  | Yes
AI121 | Peak Power Limiting Ramp Up Rate. Maximum ramp up rate | 2 | 0 | 2147483647 | 1 | 0 | Sec | 1 | DPKP |  | RmpUpRte | ING | DPKP.RmpUpRte |  | Yes
AI122 | Peak Power Limiting Ramp Down Rate. Maximum ramp down rate | 2 | 0 | 2147483647 | 1 | 0 | Sec | 1 | DPKP |  | RmpDnRte | ING | DPKP.RmpDnRte |  | Yes
AI123 | Peak Power Limiting Mode Priority |  | 0 | number of modes | 1 | 0 | n/a | 1 | DPKP |  | ModPrty | ING | DPKP.ModPrty |  | Yes
AI124 | Load Following Signal Meter ID |  | 2147483647 | 1 | 0 |  | N/A | 1 | DLFL |  | ECPRefId | ORG | DLFL.ECPRefId | Load Fol | Yes
AI125 | Load Following Reference Power Input. Active Power measurement read from the meter and used as an input to the mode. | 2 | 0 | 2147483647 | 1 | 0 | Watts | 1 | DLFL |  | WRef | MV | DLFL.WRef |  | Yes | new
AI126 | Load Following Threshhold. Threshhold to start actively following load in watts. |  | 100 | 0.001 | 0 |  | N/A | 0.001 | DLFL |  | LodFolThrshW | ASG | DLFL.LodFolThrshW |  | Yes
AI127 | Load Following Ratio. If 100%, then Load Following follows the load exactly. If < 100%, then Load Following follows the load as a percentage of the load over the threshhold. | 2 | 0 | 2147483647 | 1 | 0 | Watts | 1 | DLFL |  | PkPwrFolPct | ASG | DLFL.PkPwrFolPct |  | Yes | new
AI128 | Load Following Time Window | 2 | 0 | 2147483647 | 1 | 0 | Sec | 1 | DLFL |  | WinTms | ING | DLFL.WinTms |  | Yes
AI129 | Load Following Reversion Timeout Period | 2 | 0 | 2147483647 | 1 | 0 | Sec | 1 | DLFL |  | RevtTms | ING | DLFL.RevtTms |  | Yes
AI130 | Load Following Ramp Time | [7 empty] | DLFL |  | RmpTms | ING | DLFL.RmpTms |  | Yes
AI131 | Load Following Ramp Up Rate. Maximum ramp up rate |  | 2147483647 | 1 | 0 |  | Sec | 1 | DLFL |  | RmpUpRte | ING | DLFL.RmpUpRte |  | Yes
AI132 | Load Following Ramp Down Rate. Maximum ramp down rate | 2 | 0 | 2147483647 | 1 | 0 | Sec | 1 | DLFL |  | RmpDnRte | ING | DLFL.RmpDnRte |  | Yes
AI133 | Load Following Mode Priority | 2 | 2147483647 | 1 | 0 |  | Sec | 1 | DLFL |  | ModPrty | ING | DLFL.ModPrty |  | Yes
AI134 | Generation Following Signal Meter ID |  | 2147483647 | 1 | 0 |  | N/A | 1 | DGFL |  | ECPRefId | ORG | DGFL.ECPRefId | Gen Fol | Yes
AI135 | Generation Following Reference Power Input. Active Power measurement read from the meter and used as an input to the mode. | 2 | 0 | 2147483647 | 1 | 0 | Watts | 1 | DGFL |  | WRef | MV | DGFL.WRef |  | Yes
AI136 | Generation Following Threshhold. Threshhold to start actively following load in watts. |  | 100 | 0.001 | 0 |  | N/A | 0.001 | DGFL |  | GenFolThrshW | ASG | DGFL.GenFolThrshW |  | Yes
AI137 | Generation Following Ratio. If 100%, then Generation Following follows the generation exactly. If < 100%, then Generation Following follows the generation as a percentage of the generation over the threshhold. | 2 | 0 | 2147483647 | 1 | 0 | Watts | 1 | DGFL |  | GenFolPct | ASG | DGFL.GenFolPct |  | Yes
AI138 | Generation Following Time Window | 2 | 0 | 2147483647 | 1 | 0 | Sec | 1 | DGFL |  | WinTms | ING | DGFL.WinTms |  | Yes
AI139 | Generation Following Reversion Timeout Period | 2 | 0 | 2147483647 | 1 | 0 | Sec | 1 | DGFL |  | RevtTms | ING | DGFL.RevtTms |  | Yes
AI140 | Generation Following Ramp Time | [7 empty] | DGFL |  | RmpTms | ING | DGFL.RmpTms |  | Yes
AI141 | Generation Following Discharging Ramp Up Rate. Maximum ramp up rate (Watts) |  | 2147483647 | 1 | 0 |  | Sec | 1 | DGFL |  | RmpUpRte | ING | DGFL.RmpUpRte |  | Yes
AI142 | Generation Following Discharging Ramp Down Rate. Maximum ramp down rate | 2 | 0 | 2147483647 | 1 | 0 | Sec | 1 | DGFL |  | RmpDnRte | ING | DGFL.RmpDnRte |  | Yes
AI143 | Generation Following Charge Ramp Up Rate. Maximum ramp up rate | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DGFL |  | ChaRmpUpRte | ING | DGFL.ChaRmpUpRte |  | Yes
AI144 | Generation Following Charge Ramp Down Rate. Maximum ramp up rate | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DGFL |  | ChaRmpDnRte | ING | DGFL.ChaRmpDnRte |  | Yes
AI145 | Generation Following Mode Priority | 2 | 2147483647 | 1 | 0 |  | Sec | 1 | DGFL |  | ModPrty | ING | DGFL.ModPrty |  | Yes
AI146 | AGC Reversion Timeout Period | 2 | 0 | 2147483647 | 1 | 0 | Sec | 1 | DAGC |  | RevtTms | ING | DAGC.RevtTms |  | Yes
AI147 | AGC Active Power Target Value |  | 1 | 0.001 | 0 | 0 | kW | 1 | DAGC |  | WTgt | ASG | DAGC.WTgt |  | Yes
AI148 | AGC Signal Interval |  | 2147483647 | 1 | 0 |  | Sec | 1 | DAGC |  | PerTms | ING | DAGC.PerTms |  | Yes
AI149 | AGC Ramp Up Time. Set ramp up time by which the Active Power target is reached from then the Target Value is written |  | 2147483647 | 1 | 0 |  | Sec | 1 | DAGC |  | RmpUpTms | ING | DAGC.RmpUpTms |  | Yes
AI150 | AGC Ramp Down Time. Set ramp down time by which the Active Power target is reached from when the Target Value is written |  | 2147483647 | 1 | 0 |  | Sec | 1 | DAGC |  | RmpDnTms | ING | DAGC.RmpDnTms |  | Yes
AI151 | AGC Minimum Usable SOC. This is a range specific to AGC because the DER may be using the rest of the usable capacity for something else. Read-only. |  | 100 | 0.001 | 0 |  | Pct | 0.001 | DAGC |  | SOCUseMin | ING | DAGC.SOCUseMin |  | Yes
AI152 | AGC Maximum Usable SOC. This is a range specific to AGC because the DER may be using the rest of the usable capacity for something else. Read-only. |  | 100 | 0.001 | 0 |  | Pct | 0.001 | DAGC |  | SOCUseMax | ING | DAGC.SOCUseMax |  | Yes
AI153 | AGC Mode Priority |  | 0 | number of modes | 1 | 0 | n/a | 1 | DAGC |  | ModPrty | ING | DAGC.ModPrty |  | Yes
AI154 | Active Power Smoothing Signal Meter ID |  | 2147483647 | 1 | 0 |  | N/A | 1 | DWSM |  | ECPRefId | ORG | DWSM.ECPRefId | RPS | Yes
AI155 | Active Power Smoothing Reference Power Input. Active Power measurement read from the meter and used as an input to the mode. | 2 | 0 | 2147483647 | 1 | 0 | Watts | 1 | DWSM |  | WRef | MV | DWSM.WRef |  | Yes | new
AI156 | Active Power Smoothing Gradient. Signed quantity that establishes the ratio of additional smoothing Watts provided to the present delta-watts of the reference load or generation. Delta Watts is the difference between the moving average and the present value of the reference power. Positive values of this gradient are for following load (increased reference load results in a dynamic increase in DER output), and negative values are for following generation (increased reference generation results in a dynamic decrease in DER output). | 2 | 2147483647 | 0.001 | 0 |  | N/A | 0.001 | DWSM |  | WSmthGra | ASG | DWSM.WSmthGra |  | Yes
AI157 | Active Power Smoothing Lower Limit. Difference in Watts from the moving average of the reference power above which no smoothing shall be applied. |  | 0 | 1 | 0 |  | kW | 1 | DWSM |  | WSmthLoLim | ASG | DWSM.WSmthLoLim |  | Yes
AI158 | Active Power Smoothing Upper Limit. Difference in Watts from the moving average of the reference power below which no smoothing shall be applied. | 2 | 2147483647 | 1 | 0 |  | Watts | 1 | DWSM |  | WSmthHiLim | ASG | DWSM.WSmthHiLim |  | Yes
AI159 | Active Power Smoothing Filter Time (Seconds). Time in seconds used to calculate the moving average of the reference load or generation being smoothed. |  | 2147483647 | 1 | 0 |  | Sec | 1 | DWSM |  | FilTms | ING | DWSM.FilTms |  | Yes
AI160 | Active Power Smoothing Time Window | 2 | 2147483647 | 1 | 0 |  | Sec | 1 | DWSM |  | WinTms | ING | DWSM.WinTms |  | Yes
AI161 | Active Power Smoothing Reversion Timeout Period | 2 | 2147483647 | 1 | 0 |  | Sec | 1 | DWSM |  | RevtTms | ING | DWSM.RevtTms |  | Yes
AI162 | Active Power Smoothing Ramp Time | [7 empty] | DWSM |  | RmpTms | ING | DWSM.RmpTms |  | Yes
AI163 | Active Power Smoothing Mode Priority |  | 0 | number of modes | 1 | 0 | n/a | 1 | DWSM |  | ModPrty | ING | DWSM.ModPrty |  | Yes
AI164 | Volt-Watt Signal Meter ID |  | 2147483647 | 1 | 0 |  | N/A | 1 | DVWG |  | ECPRefId | ORG | DVWG.ECPRefId | VW51 | Yes
AI165 | Volt-Watt Reference Voltage Input. Voltage measurement read from the meter and used as an input to the mode. | [7 empty] | DVWG |  | VWRef | MV | DVWG.VWRef |  | Yes
AI166 | Volt-Watt Curve Index. Index of the Volt-Watt curve that should be used by the mode.
AI167 | Volt-Watt Decreasing Watt Gradient. Percent of WMax |  | 2147483647 | 0.001 | 0 |  | N/A | 0.001 | DVWG |  | VWDecGra | ASG | DVWG.VWDecGra |  | Yes
AI168 | Volt-Watt Increasing Watt Gradient. Percent of WMax |  | 2147483647 | 0.001 | 0 |  | N/A | 0.001 | DVWG |  | VWIncrGra | ASG | DVWG.VWIncrGra |  | Yes
AI169 | Volt-Watt Upper Limit. Positive Percent of VRef |  | 2147483647 | 0.001 | 0 |  | Volts | 0.001 | DVWG |  | VWLoLim | ASG | DVWG.VWLoLim |  | Yes
AI170 | Volt-Watt Lower Limit. Negative Percent of VRef |  | 2147483647 | 0.001 | 0 |  | Volts | 0.001 | DVWG |  | VWHiLim | ASG | DVWG.VWHiLim |  | Yes
AI171 | Volt-Watt Filter Time (Seconds) |  | 2147483647 | 1 | 0 |  | Sec | 1 | DVWG |  | FilTms | ING | DVWG.FilTms |  | Yes
AI172 | Volt-Watt Time Window |  | 2147483647 | 1 | 0 |  | Sec | 1 | DVWG |  | WinTms | ING | DVWG.WinTms |  | Yes
AI173 | Volt-Watt Reversion Timeout Period |  | 2147483647 | 1 | 0 |  | Sec | 1 | DVWG |  | RevtTms | ING | DVWG.RevtTms |  | Yes
AI174 | Volt-Watt Ramp Time | [7 empty] | DWSM |  | RmpTms | ING | DWSM.RmpTms |  | Yes
AI175 | Volt-Watt Discharging Ramp Up Rate. Maximum ramp up rate |  | 2147483647 | 1 | 0 |  | Sec | 1 | DVWG |  | RmpUpRte | ING | DVWG.RmpUpRte |  | Yes
AI176 | Volt-Watt Discharging Ramp Down Rate. Maximum ramp down rate |  | 2147483647 | 1 | 0 |  | Sec | 1 | DVWG |  | RmpDnRte | ING | DVWG.RmpDnRte |  | Yes
AI177 | Volt-Watt Charge Ramp Up Rate. Maximum charging ramp up rate | [7 empty] | DVWG |  | ChaRmpUpRte | ING | DVWG.ChaRmpUpRte |  | Yes
AI178 | Volt-Watt Charge Ramp Down Rate. Maximum charging ramp down rate | [7 empty] | DVWG |  | ChaRmpDnRte | ING | DVWG.ChaRmpDnRte |  | Yes
AI179 | Volt-Watt Mode Priority |  | 0 | number of modes | 1 | 0 | n/a | 1 | DVWG |  | ModPrty | ING | DVWG.ModPrty |  | Yes
AI180 | Frequency-Watt Mode Signal Meter ID | [7 empty] | FWHZ | 1 | ECPRefId | ASG | FWHZ1.ECPRefId | FW1 | Yes
AI181 | Frequency-Watt Mode Frequency Reference Input. Frequency measurement read from the meter and used as an input to the mode. | [7 empty] | FWHZ | 1 | HzRef | MV | FWHZ1.HzRef |  | Yes
AI182 | Frequency-Watt Mode High Speed Enable/Disable. Activation of the Active Power Reduction by Frequency function ctlVal = off (FALSE) ¦ on (TRUE) | [7 empty] | FWHZ | 1 | WCtlHzEna | ASG | FWHZ1.WCtlHzEna |  | Yes
AI183 | Frequency-Watt Mode Starting Frequency. Delta frequency between start frequency and nominal grid frequency | [7 empty] | FWHZ | 1 | HzStr | ASG | FWHZ1.HzStr |  | Yes
AI184 | Frequency-Watt Mode Stopping Frequency. Delta frequency between stop frequency and nominal grid frequency | [7 empty] | FWHZ | 1 | HzStop | ASG | FWHZ1.HzStop |  | Yes
AI185 | Frequency-Watt Mode Maximim W Change Rate. The maximum rate at which the ouput may be increased after releasing the frozen value of snap shot function. This is represented in terms of % WMax per minute. | [7 empty] | FWHZ | 1 | HzStopWGra | ASG | FWHZ1.HzStopWGra |  | Yes
AI186 | Frequency-Watt Mode Activation Delay. Intentional delay in ms before function activation | [5 empty] | ms |  | FWHZ | 1 | ActDlTmms | ING | FWHZ1.ActDlTmms |  | Yes
AI187 | Frequency-Watt Mode Hysteresis Enable/Disable. True = Use of hysteresis; False = No use of hysteresis | [7 empty] | FWHZ | 1 | HysEna | SPG | FWHZ1.HysEna |  | Yes
AI188 | Frequency-Watt Mode Snapshot of Power. True = Snapshot is active; False = Off, the snapshot is not active | [7 empty] | FWHZ | 1 | SnptW | SPG | FWHZ1.SnptW |  | Yes
AI189 | Frequency-Watt Mode Priority |  | 0 | number of modes | 1 | 0 | n/a | 1 | FWHZ | 1 | ModPrty | ING | FWHZ1.ModPrty |  | Yes
AI190 | Fixed Power Factor Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 | n/a | 1 | DFPF |  | ECPRefId | ORG | DFPF.ECPRefId | INV3 | Yes
AI191 | Fixed Power Factor Reference Power Factor Measured | [7 empty] | DFPF |  | PFRef | MV | DFPF.PFRef |  | Yes
AI192 | Fixed Power Factor Time Window | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DFPF |  | WinTms | ING | DFPF.WinTms |  | Yes
AI193 | Fixed Power Factor Reversion Timeout Period | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DFPF |  | RevtTms | ING | DFPF.RevtTms |  | Yes
AI194 | Fixed Power Factor Ramp Time | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DFPF |  | RmpTms | ING | DFPF.RmpTms |  | Yes
AI195 | Fixed Power Factor Setpoint. Meaning of sign varies depending on convention and quadrant selection settings. | 2 | -100 | 100 | 0.01 | 0 | None | 0.01 | DFPF |  | PFTgt | APC | DFPF.PFTgt |  | Yes
AI196 | Fixed Power Factor Sign convention: <1> IEC – active power <2> IEEE – lead/lag | 2 | 1 | 3 | 1 | 0 | None | 1 | DRCT |  | PFSign | ENG | DRCT.PFSign |  |  |  | Should be in DRCT? How do we know which MMXU?
AI197 | Fixed Power Factor Mode Priority |  | 0 | number of modes | 1 | 0 | n/a | 1 | DFPF |  | ModPrty | ING | DFPF.ModPrty |  | Yes
AI198 | Volt-VAr Control Signal Meter ID | 2 | 0 | 2147483647 | 1 |  |  | 1 | DVVC |  | ECPRefId | ORG | DVVC.ECPRefId | VV1,2 | Yes
AI199 | Volt-VAr Control Reference Voltage Input. Frequency measurement read from the meter and used as an input to the mode. | [7 empty] | DVVC |  | VVArRef | MV | DVVC.VVArRef |  | Yes
AI200 | Volt-VAr Curve Index. Index of the Volt-VAr curve that should be used by the mode.
AI201 | Volt-VAr Control Target Reference Voltage | [7 empty] | DVVC |  | VRef | ASG | DVVC.VRef |  | Yes
AI202 | Volt-VAr Control Time Window | 2 | 0 | 2147483647 | 1 | Seconds | Seconds | 1 | DVVC |  | WinTms | ING | DVVC.WinTms |  | Yes
AI203 | Volt-VAr Control Reversion Timeout Period | 2 | 0 | 2147483647 | 1 | Seconds | Seconds | 1 | DVVC |  | RevtTms | ING | DVVC.RevtTms |  | Yes
AI204 | Volt-VAr Control Ramp Time | 2 | 0 | 2147483647 | 1 | Seconds | Seconds | 1 | DVVC |  | RmpTms | ING | DVVC.RmpTms |  | Yes
AI205 | Volt-VAr Control Available VARs. (1=use available vars, 2=use maximum vars) | [7 empty] | DVVC |  | VVArAvl | ENG | DVVC.VVArAvl |  | Yes |  | This is set when the curves are created
AI206 | Volt-Var Mode Priority |  | 0 | number of modes | 1 | 0 | n/a | 1 | DVVC |  | ModPrty | ING | DVVC.ModPrty |  | Yes
AI207 | Watt-VAr Signal Meter ID | 2 | 0 | 2147483647 | 1 |  |  | 1 | DWVR |  | ECPRefId | ORG | DWVR.ECPRefId | W-PF | Yes |  | Exists
AI208 | Watt-VAr Reference Power Input. Power measurement read from the meter and used as an input to the mode. | [7 empty] | DWVR |  | VVArRef | MV | DWVR.VVArRef |  | Yes
AI209 | Watt-VAr Curve Index. Index of the Watt-VAr curve that should be used by the mode. | [7 empty] | DWVR | [5 empty] | Yes
AI210 | Watt-VAr Mode Priority |  | 0 | number of modes | 1 | 0 | n/a | 1 | FPFW |  | ModPrty | ING | FPFW.ModPrty |  | Yes
AI211 | Power Factor Correction Signal Meter ID | 2 | 0 | 2147483647 | 1 |  |  | 1 | DPFC |  | ECPRefId | ORG | DPFC.ECPRefId | PF-PF | Yes
AI212 | Power Factor Correction Reference Power Factor Input. Power factor measurement read from the meter and used as an input to the mode. | [7 empty] | DPFC |  | PFCorRef | MV | DPFC.PFCorRef |  | Yes
AI213 | Power Factor Correction PF Target | 2 | -1 | 1 | 0.01 | 0 | N/A | 0.01 | DPFC |  | PFTrg | ASG | DPFC.PFTrg |  | Yes |  | Not sur wat this is for
AI214 | Power Factor Correction Lower PF Limit | 2 | -1 | 1 | 0.01 | 0 | N/A | 0.01 | DPFC |  | PFCorRef.rangeC | Int | DPFC.PFCorRef.rangeC |  | Yes
AI215 | Power Factor Correction Upper PF Limit | 2 | 0 | 2147483647 | 1 | 0 | Sec | 1 | DPFC |  | PFCorRef.rangeC | Int | DPFC.PFCorRef.rangeC |  | Yes
AI216 | Power Factor Correction Time Window | 2 | 0 | 2147483647 | 1 | 0 | Sec | 1 | DPFC |  | WinTms | ING | DPFC.WinTms |  | Yes
AI217 | Power Factor Correction Reversion Timeout Period | 2 | 0 | 2147483647 | 1 | 0 | Sec | 1 | DPFC |  | RevtTms | ING | DPFC.RevtTms |  | Yes
AI218 | Power Factor Correction Ramp Time | 2 | 0 | 2147483647 | 1 | 0 | Sec | 1 | DPFC |  | RmpUpRte | ING | DPFC.RmpUpRte |  | Yes
AI219 | Power Factor Correction Mode Priority |  | 0 | number of modes | 1 | 0 | n/a | 1 | DPFC |  | ModPrty | ING | DPFC.ModPrty |  | Yes
AI220 | Pricing Mode Signal Meter ID | 2 | 0 | 2147483647 | 1 |  |  | 1 | DPRG |  | ECPRefId | ORG | DPRG.ECPRefId | INV5
AI221 | Pricing Mode Reference Pricing Input: Hundredths of local currency per Kilowatt-Hr. | [7 empty] | DPRG |  | PriceRef | MV | DPRG.PriceRef |  |  |  | Still not well-defined
AI222 | Pricing Mode Time window | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DPRG |  | WinTms | ING | DPRG.WinTms
AI223 | Pricing Mode Reversion Timeout Period | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DPRG |  | RevtTms | ING | DPRG.RevtTms
AI224 | Pricing Mode Ramp Up Time | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DPRG |  | RmpUpRte | ING | DPRG.RmpUpRte |  |  |  | Per item 70
AI225 | Pricing Mode Ramp Down Time | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DPRG |  | RmpDnRte | ING | DPRG.RmpDnRte |  |  |  | Per item 70
AI226 | Pricing Mode Priority |  | 0 | number of modes | 1 | 0 | n/a | 1 | DPRG |  | ModPrty | ING | DPRG.ModPrty
AI227 | Curve Edit Selector Index of the curve which is currently being viewed and/or changed. | 2 | 1 | 2147483647 | 1 | 0 | n/a | 1 | DGSM | n | InCrv | ORG | DGSMn.InCrv |  | Yes
AI228 | Curve Mode Type <0> Curve is not defined <1> None, dimensionless <2> Volt-Var modes VV11-VV12 <3> Frequency-Watt mode FW22 <4> Watt-VAr mode WP42 <5> Voltage-Watt modes VW51-VW52 <6> Remain Connected <7> Temperature mode <8> Pricing signal mode High Voltage ride-through curves <9> HVRT Must Trip <10> HVRT Momentary Cessation <11> HVRT Continuous Operation Low Voltage ride-through curves <12> LVRT Must Trip <13> LVRT Momentary Cessation <14> LVRT Continuous Operation High Frequency ride-through curves <15> HFRT Must Trip <16> HFRT Mandatory Operation <17> HFRT Continuous Operation Low Frequency ride-through curves <18> LFRT Must Trip <19> LFRT Mandatory Operation <20> LFRT Continuous Operation | 2 | 0 | 2147483647 | 1 | 0 | n/a | 1 | DGSM | n | ModTyp | ENG | DGSMn.ModTyp | CRV | Yes |  | Note: As of 2016, IEC 61850-7-420 has the following: None, dimensionless 1 Volt-var modes VV11 - VV12 2 Frequency-watt mode FW22 3 Watt-power-factor mode WP42 4 Voltage-watt modes VW51 - VW52 5 Remain connected 6 Temperature mode 7 Pricing signal mode 8 Low voltage ride-through mode 9 High voltage ride-through mode 10 Low frequency ride-through mode 11 High frequency ride-through mode 12 Not applicable / Unknown 98
AI229 | Curve Time Window | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DGSM | n | WinTms | ING | DGSMn.WinTms | CRV | Yes
AI230 | Curve Ramp Time | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DGSM | n | RmpTms | ING | DGSMn.RmpTms | CRV | Yes
AI231 | Curve Revert Time | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DGSM | n | RvrtTms | ING | DGSMn.RvrtTms | CRV | Yes
AI232 | Curve Number of Points | 2 | 0 | 100 | 1 | 0 | n/a | 1 | FMAR | n | PairArray. NumPts | CSG | FMARn.PairArray. NumPts | CRV | Yes
AI233 | Curve Maximum Number of Points | 2 | 0 | 100 | 1 | 0 | n/a | 1 | FMAR | n | PairArray. MaxPts | CSG | FMARn.PairArray. MaxPts | CRV | Yes
AI234 | Independent (X-Value) Units for Curve <0> Curve is not defined <1> Not applicable / Unknown <4> Time <29> Voltage <33> Frequency <38> Watts <23> Celsius Temperature <100> Price in hundredths of local currency <129> Percent Voltage <133> Percent Frequency <138> Percent Watts <233> Frequency Deviation | 2 | 0 | 233 | 1 | 0 | n/a | 1 | FMAR | n | IndpUnits | ENG | FMARn.IndpUnits | CRV | Yes
AI235 | Dependent (Y-Value) Units for Curve <0> Curve is not defined <1> Not applicable / unknown <2> VArs as percent of max VArs (VARMax) <3> VArs as percent of max available VArs (VArAval) <4> Vars as percent of max Watts (Wmax) - not used <5> Watts as percent of max Watts (Wmax) <6> Watts as percent of frozen active power (DeptSnptRef) <7> Power Factor in EEI notation <8> Volts as a percent of the nominal voltage (VRef) <99+> Other | 2 | 0 | 255 | 1 | 0 | n/a | 1 | FMAR | n | DeptRef | ENG | FMARn.DeptRef | CRV | Yes | new
AI236 | Curve Time Constant. Time constant of the low-pass filter to be applied to the output of the Curve, in seconds. This is the 3T (tau) value specifying the time at which a step change of the Dependent Variable (e.g. Watts) will settle to 95% of the final value. | 2 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | FMAR | n | RmpPT1Tms | ENG | FMARn.RmpPT1Tms | CRV | Yes | new | Optional. Should we include?
AI237 | Curve Decreasing Max Ramp Rate. The maximum rate at which the dependent value (output, Y-Value) may be reduced in response to changes in the independent value (input, X-Value). This is represented in terms of % of Reference value (e.g. WMax) per minute . | 2 | 0 | 1000 | 0.1 | 0 | Percent per min |  | FMAR | n | RmpDecDmm | ENG | FMARn.RmpDecDmm | CRV | Yes | new | Optional. Should we include?
AI238 | Curve Increasing Max Ramp Rate. The maximum rate at which the dependent value (output, Y-Value) may be reduced in response to changes in the independent value (input, X-Value). This restriction is applied after the low-pass filter. This value is represented in terms of % of Reference value (e.g. WMax) per minute . | 2 | 0 | 1000 | 0.1 | 0 | Percent per min | 1 | FMAR | n | RmpIncTmm | ENG | FMARn.RmpIncTmm | CRV | Yes | new | Optional. Should we include?
AI239 | Curve Release Max Ramp Rate. The maximum rate at which the dependent value (ouput, Y-Value) may be increased after releasing the frozen value of snap shot function. This restriction is applied after the low-pass filter. This value is represented in terms of % of Reference value (e.g. WMax) per minute. | 2 | 0 | 1000 | 0.1 | 0 | Percent per min | 1 | FMAR | n | RmpRsUp | ENG | FMARn.RmpRsUp | CRV | Yes | new | Optional. Should we include?
AI240 | Curve Dependent Variable Snapshot Reference. This is the snapshot value of the dependent variable (Y-Value, e.g. Watts) stored when the independent variable (X-Value, e.g. Frequency) reaches a threshold value. Currently only used with Curve Mode Type <223> Frequency Deviation. | 2 | Varies depending on Curve Mode Type |  |  | 0 | Varies | Varies | FMAR | n | DeptSnptRef | MV | FMARn.DeptSnptRef | FW22 | Yes | new
AI241 | Curve Dependent Variable Snapshot Start. Deviation from nominal value of the independent variable (X-Value, e.g. Frequency) at which to take a snapshot of the dependent variable (e.g. WRef) and start constraining the output ( e.g. Watts). Currently only used with Independent Value Units of <223> Frequency Deviation. | 2 | see table depending on Mode Type |  |  | 0 | Varies | (1%) | FMAR | n | DeptRefStr | ENG | FMARn.DeptRefStr | FW22 | Yes
AI242 | Curve Dependent Variable Snapshot Stop. Deviation from nominal value of the independent variable (X-Value, e.g. Frequency) at which to release the output (Y-Value, e.g. Watts). Currently only used with Independent Curve Units of <223> Frequency Deviation. | 2 | see table depending on Mode Type |  |  | 0 | Varies | (1%) | FMAR | n | DeptRefStop | ENG | FMARn.DeptRefStop | FW22 | Yes | new | Optional. Should we include?
AI243 | Curve Point 1 X-Value | 2 | see scaling table depending on Mode Type |  |  | 0 | Varies | 1 | FMAR | n | PairArray.CrvPts[0].xVal | CSG | FMARn.PairArray.CrvPts[0].xVal | CRV | Yes | new
AI244 | Curve Point 1 Y-Value | 2 | see scaling table depending on Mode Type |  |  | 0 | Varies | 1 | FMAR | n | PairArray.CrvPts[0].yVal | CSG | FMARn.PairArray.CrvPts[0].yVal | CRV | Yes | new
AI245 | Curve Point 2 X-Value | 2 | see scaling table depending on Mode Type |  |  | 0 | Varies | 1 | FMAR | n | PairArray.CrvPts[1].xVal | CSG | FMARn.PairArray.CrvPts[1].xVal | CRV | Yes | new
AI246 | Curve Point 2 Y-Value | 2 | see scaling table depending on Mode Type |  |  | 0 | Varies | 1 | FMAR | n | PairArray.CrvPts[1].yVal | CSG | FMARn.PairArray.CrvPts[1].yVal | CRV | Yes | new
AI247 - AI436 | Curve X-Value, Y-Value pairs for curve points 3 -99 | [11 empty] | . |  | Yes
AI437 | Curve Point 100 X-Value | 2 | see scaling table depending on Mode Type |  |  | 0 | Varies | 1 | FMAR | n | PairArray.CrvPts[100].xVal | CSG | FMARn.PairArray.CrvPts[100].xVal | CRV | Yes | new
AI438 | Curve Point 100 Y-Value | 2 | see scaling table depending on Mode Type |  |  | 0 | Varies | 1 | FMAR | n | PairArray.CrvPts[100].yVal | CSG | FMARn.PairArray.CrvPts[100].yVal | CRV | Yes | new
S (S=446 for this version of the specifcation) | Running Schedule Index. Index of the highest priority schedule that is currently running. | 2 | 0 | 2147483647 | 1 | 0 | n/a | 1 | FSCC | 1 | CtlSchdSt | ORG | FSCC1.CtlSchdSt | SCHED | Yes | new
#REF! | Schedule to Edit Selector | 3 | 0 | 2147483647 | 1 | 0 | N/A | 1 |  |  |  |  | . |  | Yes |  | From MESA points
S+1 | Selected Schedule Priority | 3 | 1 | 2147483647 | 1 | 0 | N/A | 1 |  |  |  |  | . |  | Yes |  | From MESA points
#REF! | Selected Schedule Type (yVal) <0> Not applicable / Unknown <1> Active power (2.3.4), Percent of maximum <2> Reserved <3> Power factor ( 2.3.5) <4> Reserved <5> Price for active power (2.3.7) <6> Price for reactive power <7> Reserved <8> Curve Identifier (2.3.6) (previously Volt/VAR Array) <9> Charge/Discharge rate (2.3.6), percent of maximum <10> State of Charge (percent of full charge) <11> Power factor correction (on/off) <12> Peak Power Limiting (on/off) <13> Load or Generation following (on/off) | 3 | 0 | 2147483647 | 1 | 0 | N/A | 1 |  |  |  |  | . |  | Yes |  | From MESA points
#REF! | Selected Schedule Start Time Long 1. Upper 32 bits of 64-bit Date/time expressed as the number of seconds January 1st, 1970. | 3 | 0 | 2147483647 | 1 | 0 | Edate | 1 |  |  |  |  | . |  | Yes |  | From MESA points
S+2 | Selected Schedule Start Time Long 2. Lower 32 bits of 64-bit Date/time expressed as the number of seconds from January 1st, 1970. | 3 | 0 | 2147483647 | 1 | 0 | Edate | 1 |  |  |  |  | . |  | Yes |  | From MESA points
S+3 | Selected Schedule Repeat Interval | 3 | 0 | 2147483647 | 1 | 0 | Varies | 1 |  |  |  |  | . |  | Yes |  | From MESA points
S+4 | Selected Schedule Repeat Interval Units | 3 | 0 | 8 | 1 | 0 | N/A | 1 |  |  |  |  | . |  | Yes |  | From MESA points
S+5 | Selected Schedule Validation Status | 3 | 0 | 4 | 1 | 0 | N/A | 1 |  |  |  |  | . |  | Yes |  | From MESA points
S+6 | Selected Schedule Status <0> unknown <1> Not available <2> Inactive <3> Ready-to-Run <4> Running | 2 | 0 | 4 | 1 | 0 | n/a | 1 | FSCH | 1 | SchSt | ENS | FSCH1.SchSt | SCHED | Yes | new | From DNP3 points
S+7 | Selected Schedule Number of Points | 3 | 0 | 2147483647 | 1 | 0 | N/A | 1 |  |  |  |  | . |  | Yes |  | From MESA points
S+8 | Schedule 1 Status <0> unknown <1> Not available <2> Inactive <3> Ready-to-Run <4> Running | 2 | 0 | 4 | 1 | 0 | n/a | 1 | FSCH | 1 | SchSt | ENS | FSCH1.SchSt | SCHED | Yes | new | From DNP3 points
S+9 | Schedule 1 Priority | 2 | 1 | Number of possible schedules | 1 | 0 | n/a | [5 empty] | . |  | Yes | new
S+10 | Schedule 1 Active Time Value. This is the index of the time value entry the schedule is currently running. First entry is 1. Zero if the schedule is not running. | 2 | 0 | 10 | 1 | 0 | n/a | 1 | FSCH | 1 | ActSchEntr | INS | FSCH1.ActSchEntr | SCD | Yes | new
. . . | Schedule #2 . . . Schedule #s-1 points | 2 | 0 | 4 | 1 | 0 | n/a | 1 | [7 empty] | new
S+(3(s-1) + 13) | Schedule #s Status | 2 | 0 | 4 | 1 | 0 | n/a | 1 | FSCH | 1 | SchSt | ENS | FSCH1.SchSt | SCHED | Yes | new
S+(3(s-1) + 14) | Schedule #s Priority | 2 | 1 | Number of possible schedules | 1 | 0 | n/a | [5 empty] | . |  | Yes | new
S+(3(s-1) + 15) | Schedule #s Active ime Value. | 2 | 0 | 10 | 1 | 0 | n/a | 1 | FSCH | 1 | ActSchEntr | INS | FSCH1.ActSchEntr | SCD | Yes | new
S+(3(s-1) + 16) | Selected Schedule Point [1] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | varies | 1 | FSCH | n | SchdVal.val[ 1 ] |  | FSCHn.SchdVal.val[ 1 ] |  | Yes
S+(3(s-1) + 17) | Selected Schedule Point[1] Value |  | -2147483648 | 2147483647 | 1 | 0 | Seconds | 1 |  |  |  |  | . |  | Yes
| Selected Schedule Point [2, 99] Time Offsets | [11 empty] | . |  | Yes
S+3(s-1) + 115 | Selected Schedule Point[100] Value |  | -2147483648 | 2147483647 | 1 | 0 | Seconds | 1 |  |  |  |  | . |  | Yes
S+3(s-1) + 116 | Selected Schedule Point [100] Time Offset | 2 | 0 | 2147483647 | 1 | 0 | varies | 1 | FSCH | n | SchdVal.val[ 1 ] |  | FSCHn.SchdVal.val[ 1 ] |  | Yes
HM | Meter #1 Type of connection point: <0> unknown, <1> DER to local load, <2> DER to local EPS, <3> local EPS with load to area EPS, <4> local EPS w/o load to area EPS <5> other. Most likely value is <1> | 3 | 1 | 5 | 1 | 0 | None (list) | 1 | DOPR |  | ECPType | ENS | DOPR.ECPType |  | Yes
#REF! | Meter #1 Frequency at the connection point | 3 | 0 | 70000 | 0.001 | 0 | Hz | 0.001 | MMXU |  | Hz | MV | MMXU.Hz |  | Yes
HM+1 | Meter #1 Active power at the connection point | 3 | -2147483648 | 2147483647 | 1 | 0 | Watts | (1%) | MMXU |  | TotW | MV | MMXU.TotW |  | Yes
#REF! | Meter #1 Reactive power at connection point | 3 | -2147483648 | 2147483647 | 1 | 0 | VARs | (1%) | MMXU |  | TotVAr | MV | MMXU.TotVAr |  | Yes
#REF! | Meter #1 Power factor at the connection point | 3 | -100 | 100 | 0.01 | 0 | n/a | 0.01 | MMXU |  | TotPF | MV | MMXU.TotPF |  | Yes
HM+2 | Meter #1 Apparent power at the connection point | 3 | -2147483648 | 2147483647 | 1 | 0 | VA | (1%) | MMXU |  | TotVA | MV | MMXU.TotVA |  | Yes | new
HM+3 | Meter #1 Phase A Volts at connection point | 3 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMXU |  | PhV.phsA.mag | WYE | MMXU.PhV.phsA.mag |  | Yes
HM+4 | Meter #1 Phase A Volts angle at connection point | 3 | 0 | 3600 | 0.1 | 0 | Degrees | 0.1 | MMXU |  | PhV.phsA.ang | WYE | MMXU.PhV.phsA.ang |  | Yes
HM+5 | Meter #1 Phase B Volts at connection point | 3 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMXU |  | PhV.phsB.mag | WYE | MMXU.PhV.phsB.mag |  | Yes
HM+6 | Meter #1 Phase B Volts angle at connection point | 3 | 0 | 3600 | 0.1 | 0 | Degrees | 0.1 | MMXU |  | PhV.phsB.ang | WYE | MMXU.PhV.phsB.ang |  | Yes
HM+7 | Meter #1 Phase C Volts at connection point | 3 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMXU |  | PhV.phsC.mag | WYE | MMXU.PhV.phsC.mag |  | Yes
HM+8 | Meter #1 Phase C Volts angle at connection point | 3 | 0 | 3600 | 0.1 | 0 | Degrees | 0.1 | MMXU |  | PhV.phsC.ang | WYE | MMXU.PhV.phsC.ang |  | Yes
HM+9 | Meter #1 Type of circuit phases: <0> unknown <1> single phase <2> 3-phase <3> delta <4> wye <5> wye-grounded <6> other | 3 | 1 | 6 | 1 | 0 | None (list) | 1 | DOPR |  | CctPhs | ENS | DOPR.CctPhs |  | Yes
HM+10 | Meter #1 Reference Voltage at ECP |  | 0 | 2147483647 | 1 | 0 | Volts | (1%) | DOPR |  | ECPVRef | ASG | DOPR.ECPVRef |  | Yes |  | Voltage references should be per ECP, and therefore not DRCT
HM+11 | Meter #1 Reference Voltage Offset at ECP |  | 0 | 2147483647 | 1 | 0 | Volts | (1%) | DOPR |  | ECPVRefOfs | ASG | DOPR.ECPVRefOfs |  | Yes
HM+12 | Meter #1 Active power at connection point – high threshold |  | 0 | 2147483647 | 1 | 0 | Watts | (1%) | MMXU |  | TotW.rangeC.hLim | MV | MMXU.TotW.rangeC.hLim |  | Yes |  | I assume (??) these are settings, not measurements?
HM+13 | Meter #1 Active power at connection point – low threshold |  | 0 | 2147483647 | 1 | 0 | Watts | (1%) | MMXU |  | TotW.rangeC.lLim | MV | MMXU.TotW.rangeC.lLim |  | Yes
HM+14 | Meter #1 Reactive power at connection point – high threshold |  | 0 | 2147483647 | 1 | 0 | VARs | (1%) | MMXU |  | TotVAr.rangeC.hLim | MV | MMXU.TotVAr.rangeC.hLim |  | Yes
HM+16 | Meter #1 Reactive power at connection point – low threshold |  | 0 | 2147483647 | 1 | 0 | VARs | (1%) | MMXU |  | TotVAr.rangeC.lLim | MV | MMXU.TotVAr.rangeC.lLim |  | Yes
HM+15 | Meter #1 Power factor at connection point – high threshold |  | -100 | 100 | 0.01 | 0 | None | 0.01 | MMXU |  | TotPF.rangeC.hLim | MV | MMXU.TotPF.rangeC.hLim |  | Yes
HM+17 | Meter #1 Power factor at connection point – low threshold |  | -100 | 100 | 0.01 | 0 | None | 0.01 | MMXU |  | TotPF.rangeC.lLim | MV | MMXU.TotPF.rangeC.lLim |  | Yes
HM+20 | Meter #1 Phase A Volts – high threshold |  | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMXU |  | PhV.phsA.rangeC.hLim | WYE | MMXU.PhV.phsA.rangeC.hLim |  | Yes
HM+21 | Meter #1 Phase A Volts – low threshold |  | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMXU |  | PhV.phsA.rangeC.lLim | WYE | MMXU.PhV.phsA.rangeC.lLim |  | Yes
HM+19 | Meter #1 Phase B Volts – high threshold |  | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMXU |  | PhV.phsB.rangeC.hLim | WYE | MMXU.PhV.phsB.rangeC.hLim |  | Yes
HM+22 | Meter #1 Phase B Volts – low threshold |  | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMXU |  | PhV.phsB.rangeC.lLim | WYE | MMXU.PhV.phsB.rangeC.lLim |  | Yes
HM+23 | Meter #1 Phase C Volts – high threshold |  | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMXU |  | PhV.phsC.rangeC.hLim | WYE | MMXU.PhV.phsC.rangeC.hLim |  | Yes
HM+24 | Meter #1 Phase C Volts – low threshold |  | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMXU |  | PhV.phsC.rangeC.lLim | WYE | MMXU.PhV.phsC.rangeC.lLim |  | Yes
HM+25 | Meter #1 Active Power (in kW) | 1 | -2147483648 | 2147483647 | 1 | 0 | kW | 1 |  |  |  |  | . |  | Yes |  | What are these? They seem to be the same as above but just in kxx
HM+26 | Meter #1 Reactive Power (in kVAR) | 1 | -2147483648 | 2147483647 | 1 | 0 | kVAR | 1 |  |  |  |  | . |  | Yes
HM+27 | Meter #1 Apparent Power (kVA) | 1 | -2147483648 | 2147483647 | 1 | 0 | kVA | 1 |  |  |  |  | . |  | Yes
HM+28 | Meter #1 Power Factor | 1 | -1 | 1 | 0.01 | 0 | N/A | 0.01 | MMXU |  | TotPF |  | MMXU.TotPF |  | Yes
HM+29 | Meter #1 Frequency (in Hz) | 1 | 0 | 2147483647 | 0.001 | 0 | Hertz | 0.001 | MMXU |  | HZ |  | MMXU.HZ |  | Yes |  | Are these separate values from those "at the connection point"?
HM+30 | Meter #1 Voltage A (in Volts) | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | 0.001 | MMXU |  | PhV.phsA.mag |  | MMXU.PhV.phsA.mag |  | Yes
HM+31 | Meter #1 Voltage B (in Volts) | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | 0.001 | MMXU |  | PhV.phsB.mag |  | MMXU.PhV.phsB.mag |  | Yes
HM+32 | Meter #1 Voltage C (in Volts) | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | 0.001 | MMXU |  | PhV.phsC.mag |  | MMXU.PhV.phsC.mag |  | Yes
HM+33 | Meter #1 Average Line to Line Voltage (in Volts) | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | 0.001 | MMXU |  | AvPPVPhs |  | MMXU.AvPPVPhs |  | Yes
#REF! | Meter #1 Current A (in Amps) | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | 0.1 | MMXU |  | A.phsA.mag |  | MMXU.A.phsA.mag |  | Yes
#REF! | Meter #1 Current B (in Amps) | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | 0.1 | MMXU |  | A.phsB.mag |  | MMXU.A.phsB.mag |  | Yes
HM+34 | Meter #1 Current C (in Amps) | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | 0.1 | MMXU |  | A.phsC.mag |  | MMXU.A.phsC.mag |  | Yes
HM+35 | Meter #1 Active Power A (in kW) | 1 | -2147483648 | 2147483647 | 1 | 0 | kW | 1 |  |  |  |  | . |  | Yes
HM+36 | Meter #1 Active Power B (in kW) | 1 | -2147483648 | 2147483647 | 1 | 0 | kW | 1 |  |  |  |  | . |  | Yes
HM+37 | Meter #1 Active Power C (in kW) | 1 | -2147483648 | 2147483647 | 1 | 0 | kW | 1 |  |  |  |  | . |  | Yes
HM+38 | Meter #1 Reactive Power A (in kVAR) | 1 | -2147483648 | 2147483647 | 1 | 0 | kVAR | 1 |  |  |  |  | . |  | Yes
HM+39 | Meter #1 Reactive Power B (in kVAR) | 1 | -2147483648 | 2147483647 | 1 | 0 | kVAR | 1 |  |  |  |  | . |  | Yes
HM+44 | Meter #1 Reactive Power C (in kVAR) | 1 | -2147483648 | 2147483647 | 1 | 0 | kVAR | 1 |  |  |  |  | . |  | Yes
HM+45 | Meter #1 Maximum Active Power capability | 2 | 0 | 2147483647 | 1 | 0 | Watts | (1%)% | DRCT |  | WMax | ASG | DRCT.WMax | INV2 | Yes | New IEC 61850 name | Was MaxWLim. What purpose does this have since meters only measure?
HM+46 | Meter #1 Reference Voltage | 2 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | DOPR |  | ECPVRef | ASG | DOPR.ECPVRef | VV11-14 | Yes |  | These seem to be duplicates
HM+47 | Meter #1 Reference Voltage Offset | 2 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | DOPR |  | ECPVRefOfs | ASG | DOPR.ECPVRefOfs | VV11-14 | Yes |  | These seem to be duplicates
HM+48 | Meter #1 Active power at connection point – high threshold | 2 | 0 | 2147483647 | 1 | 0 | Watts | (1%) | MMXU |  | TotW.RangeC.hLim | MV | MMXU.TotW.RangeC.hLim |  | Yes |  | What does high and low threshold mean? Are these the limits? If so, they are range configuration settings
HM+87 | Meter #1 Active power at connection point – low threshold | 2 | 0 | 2147483647 | 1 | 0 | Watts | (1%) | MMXU |  | TotW.RangeC.lLim | MV | MMXU.TotW.RangeC.lLim |  | Yes
HM+88 | Meter #1 Reactive power at connection point – high threshold | 2 | 0 | 2147483647 | 1 | 0 | VARs | (1%) | MMXU |  | TotVAr.rangeC.hLim | MV | MMXU.TotVAr.rangeC.hLim |  | Yes
HM+89 | Meter #1 Reactive power at connection point – low threshold | 2 | 0 | 2147483647 | 1 | 0 | VARs | (1%) | MMXU |  | TotVAr.rangeC.lLim | MV | MMXU.TotVAr.rangeC.lLim |  | Yes
HM+90 | Meter #1 Power factor at connection point – high threshold | 2 | -100 | 100 | 0.01 | 0 | None | 0.01 | MMXU |  | TotPF.rangeC.hLim | MV | MMXU.TotPF.rangeC.hLim |  | Yes
HM+91 | Meter #1 Power factor at connection point – low threshold | 2 | -100 | 100 | 0.01 | 0 | None | 0.01 | MMXU |  | TotPF.rangeC.lLim | MV | MMXU.TotPF.rangeC.lLim |  | Yes
HM+92 | Meter #1 Phase A Volts – high threshold | 2 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMXU |  | PhV.phsA.rangeC.hLim | WYE | MMXU.PhV.phsA.rangeC.hLim |  | Yes
HM+93 | Meter #1 Phase A Volts – low threshold | 2 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMXU |  | PhV.phsA.rangeC.lLim | WYE | MMXU.PhV.phsA.rangeC.lLim |  | Yes
HM+94 | Meter #1 Phase B Volts – high threshold | 2 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMXU |  | PhV.phsB.rangeC.hLim | WYE | MMXU.PhV.phsB.rangeC.hLim |  | Yes
HM+57 | Meter #1 Phase B Volts – low threshold | 2 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMXU |  | PhV.phsB.rangeC.lLim | WYE | MMXU.PhV.phsB.rangeC.lLim |  | Yes
HM+58 | Meter #1 Phase C Volts – high threshold | 2 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMXU |  | PhV.phsC.rangeC.hLim | WYE | MMXU.PhV.phsC.rangeC.hLim |  | Yes
HM+59 | Meter #1 Phase C Volts – low threshold | 2 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMXU |  | PhV.phsC.rangeC.lLim | WYE | MMXU.PhV.phsC.rangeC.lLim |  | Yes
. . . | Meter #2 . . . #m points | [11 empty] | . |  | Yes
HM+ mhai(m-1) | Meter #m Type of connection point | 3 | 1 | 5 | 1 | 0 | None (list) | 1 | DOPR |  | ECPType | ENS | DOPR.ECPType |  | Yes
#REF! | Meter #m Frequency at the connection point | 3 | 0 | 70000 | 0.001 | 0 | Hz | 0.001 | MMXU |  | Hz | MV | MMXU.Hz |  | Yes
HM+ mhai(m-1)+1 | Meter #m Active power at the connection point | 3 | -2147483648 | 2147483647 | 1 | 0 | Watts | (1%) | MMXU |  | TotW | MV | MMXU.TotW |  | Yes
#REF! | Meter #m Reactive power at connection point | 3 | -2147483648 | 2147483647 | 1 | 0 | VARs | (1%) | MMXU |  | TotVAr | MV | MMXU.TotVAr |  | Yes
#REF! | Meter #m Power factor at the connection point | 3 | -100 | 100 | 0.01 | 0 | n/a | 0.01 | MMXU |  | TotPF | MV | MMXU.TotPF |  | Yes
HM+ mhai(m-1)+2 | Meter #m Apparent power at the connection point | 3 | -2147483648 | 2147483647 | 1 | 0 | VA | (1%) | MMXU |  | TotVA | MV | MMXU.TotVA |  | Yes | new
HM+ mhai(m-1)+3 | Meter #m Phase A Volts at connection point | 3 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMXU |  | PhV.PhsA.mag | WYE | MMXU.PhV.PhsA.mag |  | Yes
HM+ mhai(m-1)+4 | Meter #m Phase A Volts angle at connection point | 3 | 0 | 3600 | 0.1 | 0 | Degrees | 0.1 | MMXU |  | PhV.PhsA.ang | WYE | MMXU.PhV.PhsA.ang |  | Yes
HM+ mhai(m-1)+5 | Meter #m Phase B Volts at connection point | 3 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMXU |  | PhV.PhsB.mag | WYE | MMXU.PhV.PhsB.mag |  | Yes
HM+ mhai(m-1)+6 | Meter #m Phase B Volts angle at connection point | 3 | 0 | 3600 | 0.1 | 0 | Degrees | 0.1 | MMXU |  | PhV.PhsB.ang | WYE | MMXU.PhV.PhsB.ang |  | Yes
HM+ mhai(m-1)+7 | Meter #m Phase C Volts at connection point | 3 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMXU |  | PhV.PhsC.mag | WYE | MMXU.PhV.PhsC.mag |  | Yes
HM+ mhai(m-1)+8 | Meter #m Phase C Volts angle at connection point | 3 | 0 | 3600 | 0.1 | 0 | Degrees | 0.1 | MMXU |  | PhV.PhsC.ang | WYE | MMXU.PhV.PhsC.ang |  | Yes
HM+ mhai(m-1)+9 | Meter #m Type of circuit phases | 3 | 1 | 6 | 1 | 0 | None (list) | 1 | DOPR |  | CctPhs | ENS | DOPR.CctPhs |  | Yes
HM+ mhai(m-1)+10 | Meter #m Reference Voltage |  | 0 | 2147483647 | 1 | 0 | Volts | (1%) | DRCT |  | Vref | ASG | DRCT.Vref |  | Yes
HM+ mhai(m-1)+11 | Meter #m Reference Voltage Offset |  | 0 | 2147483647 | 1 | 0 | Volts | (1%) | DRCT |  | VrefOfs | ASG | DRCT.VrefOfs |  | Yes
HM+ mhai(m-1)+12 | Meter #m Active power at connection point – high threshold |  | 0 | 2147483647 | 1 | 0 | Watts | (1%) | MMXU |  | TotW | MV | MMXU.TotW |  | Yes
HM+ mhai(m-1)+13 | Meter #m Active power at connection point – low threshold |  | 0 | 2147483647 | 1 | 0 | Watts | (1%) | MMXU |  | TotW | MV | MMXU.TotW |  | Yes
HM+ mhai(m-1)+14 | Meter #m Reactive power at connection point – high threshold |  | 0 | 2147483647 | 1 | 0 | VARs | (1%) | MMXU |  | TotVAr | MV | MMXU.TotVAr |  | Yes
HM+ mhai(m-1)+16 | Meter #m Reactive power at connection point – low threshold |  | 0 | 2147483647 | 1 | 0 | VARs | (1%) | MMXU |  | TotVAr | MV | MMXU.TotVAr |  | Yes
HM+ mhai(m-1)+15 | Meter #m Power factor at connection point – high threshold |  | -100 | 100 | 0.01 | 0 | None | 0.01 | MMXU |  | TotPF | MV | MMXU.TotPF |  | Yes
HM+ mhai(m-1)+17 | Meter #m Power factor at connection point – low threshold |  | -100 | 100 | 0.01 | 0 | None | 0.01 | MMXU |  | TotPF | MV | MMXU.TotPF |  | Yes
HM+ mhai(m-1)+20 | Meter #m Phase A Volts – high threshold |  | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMXU |  | PhV | WYE | MMXU.PhV |  | Yes
HM+ mhai(m-1)+21 | Meter #m Phase A Volts – low threshold |  | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMXU |  | PhV | WYE | MMXU.PhV |  | Yes
HM+ mhai(m-1)+19 | Meter #m Phase B Volts – high threshold |  | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMXU |  | PhV | WYE | MMXU.PhV |  | Yes
HM+ mhai(m-1)+22 | Meter #m Phase B Volts – low threshold |  | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMXU |  | PhV | WYE | MMXU.PhV |  | Yes
HM+ mhai(m-1)+23 | Meter #m Phase C Volts – high threshold |  | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMXU |  | PhV | WYE | MMXU.PhV |  | Yes
HM+ mhai(m-1)+24 | Meter #m Phase C Volts – low threshold |  | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMXU |  | PhV | WYE | MMXU.PhV |  | Yes
HM+ mhai(m-1)+25 | Meter #m Active Power (in kW) | 1 | -2147483648 | 2147483647 | 1 | 0 | kW | 1 |  |  |  |  | . |  | Yes
HM+ mhai(m-1)+26 | Meter #m Reactive Power (in kVAR) | 1 | -2147483648 | 2147483647 | 1 | 0 | kVAR | 1 |  |  |  |  | . |  | Yes
HM+ mhai(m-1)+27 | Meter #m Apparent Power (kVA) | 1 | -2147483648 | 2147483647 | 1 | 0 | kVA | 1 |  |  |  |  | . |  | Yes
HM+ mhai(m-1)+28 | Meter #m Power Factor | 1 | -1 | 1 | 0.01 | 0 | N/A | 0.01 |  |  |  |  | . |  | Yes
HM+ mhai(m-1)+29 | Meter #m Frequency (in Hz) | 1 | 0 | 2147483647 | 0.001 | 0 | Hertz | 0.001 |  |  |  |  | . |  | Yes
HM+ mhai(m-1)+30 | Meter #m Voltage A (in Volts) | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | 0.001 |  |  |  |  | . |  | Yes
HM+ mhai(m-1)+31 | Meter #m Voltage B (in Volts) | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | 0.001 |  |  |  |  | . |  | Yes
HM+ mhai(m-1)+32 | Meter #m Voltage C (in Volts) | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | 0.001 |  |  |  |  | . |  | Yes
HM+ mhai(m-1)+33 | Meter #m Average Line to Line Voltage (in Volts) | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | 0.001 |  |  |  |  | . |  | Yes
#REF! | Meter #m Current A (in Amps) | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | 0.1 |  |  |  |  | . |  | Yes
#REF! | Meter #m Current B (in Amps) | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | 0.1 |  |  |  |  | . |  | Yes
HM+ mhai(m-1)+34 | Meter #m Current C (in Amps) | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | 0.1 |  |  |  |  | . |  | Yes
HM+ mhai(m-1)+35 | Meter #m Active Power A (in kW) | 1 | -2147483648 | 2147483647 | 1 | 0 | kW | 1 |  |  |  |  | . |  | Yes
HM+ mhai(m-1)+36 | Meter #m Active Power B (in kW) | 1 | -2147483648 | 2147483647 | 1 | 0 | kW | 1 |  |  |  |  | . |  | Yes
HM+ mhai(m-1)+37 | Meter #m Active Power C (in kW) | 1 | -2147483648 | 2147483647 | 1 | 0 | kW | 1 |  |  |  |  | . |  | Yes
HM+ mhai(m-1)+38 | Meter #m Reactive Power A (in kVAR) | 1 | -2147483648 | 2147483647 | 1 | 0 | kVAR | 1 |  |  |  |  | . |  | Yes
HM+ mhai(m-1)+39 | Meter #m Reactive Power B (in kVAR) | 1 | -2147483648 | 2147483647 | 1 | 0 | kVAR | 1 |  |  |  |  | . |  | Yes
HM+ mhai(m-1)+44 | Meter #m Reactive Power C (in kVAR) | 1 | -2147483648 | 2147483647 | 1 | 0 | kVAR | 1 |  |  |  |  | . |  | Yes
HM+ mhai(m-1)+45 | Meter #m Maximum Active Power capability | 2 | 0 | 2147483647 | 1 | 0 | Watts | (1%)% | DRCT |  | WMax | ASG | DRCT.WMax | INV2 | Yes | New IEC 61850 name | Was MaxWLim
HM+ mhai(m-1)+46 | Meter #m Reference Voltage | 2 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | DRCT |  | Vref | ASG | DRCT.Vref | VV11-14 | Yes
HM+ mhai(m-1)+47 | Meter #m Reference Voltage Offset | 2 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | DRCT |  | VrefOfs | ASG | DRCT.VrefOfs | VV11-14 | Yes
HM+ mhai(m-1)+48 | Meter #m Active power at connection point – high threshold | 2 | 0 | 2147483647 | 1 | 0 | Watts | (1%) | MMXU |  | TotW | MV | MMXU.TotW |  | Yes
HM+ mhai(m-1)+87 | Meter #m Active power at connection point – low threshold | 2 | 0 | 2147483647 | 1 | 0 | Watts | (1%) | MMXU |  | TotW | MV | MMXU.TotW |  | Yes
HM+ mhai(m-1)+88 | Meter #m Reactive power at connection point – high threshold | 2 | 0 | 2147483647 | 1 | 0 | VARs | (1%) | MMXU |  | TotVAr | MV | MMXU.TotVAr |  | Yes
HM+ mhai(m-1)+89 | Meter #m Reactive power at connection point – low threshold | 2 | 0 | 2147483647 | 1 | 0 | VARs | (1%) | MMXU |  | TotVAr | MV | MMXU.TotVAr |  | Yes
HM+ mhai(m-1)+90 | Meter #m Power factor at connection point – high threshold | 2 | -100 | 100 | 0.01 | 0 | None | 0.01 | MMXU |  | TotPF | MV | MMXU.TotPF |  | Yes
HM+ mhai(m-1)+91 | Meter #m Power factor at connection point – low threshold | 2 | -100 | 100 | 0.01 | 0 | None | 0.01 | MMXU |  | TotPF | MV | MMXU.TotPF |  | Yes
HM+ mhai(m-1)+92 | Meter #m Phase A Volts – high threshold | 2 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMXU |  | PhV | WYE | MMXU.PhV |  | Yes
HM+ mhai(m-1)+93 | Meter #m Phase A Volts – low threshold | 2 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMXU |  | PhV | WYE | MMXU.PhV |  | Yes
HM+ mhai(m-1)+94 | Meter #m Phase B Volts – high threshold | 2 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMXU |  | PhV | WYE | MMXU.PhV |  | Yes
HM+ mhai(m-1)+57 | Meter #m Phase B Volts – low threshold | 2 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMXU |  | PhV | WYE | MMXU.PhV |  | Yes
HM+ mhai(m-1)+58 | Meter #m Phase C Volts – high threshold | 2 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMXU |  | PhV | WYE | MMXU.PhV |  | Yes
HM+ mhai(m-1)+59 | Meter #m Phase C Volts – low threshold | 2 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMXU |  | PhV | WYE | MMXU.PhV |  | Yes
HDU | DER Unit #1 Number of hours the DER has been connected to the power system | 3 | 0 | 2147483647 | 1 | 0 | Hours | 1 | DRCS |  | OpTmh | INS | DRCS.OpTmh |  | Yes
#REF! | DER Unit #1 Operational time in seconds since commissioning | 3 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DPST |  | OpTms | INS | DPST.OpTms |  | Yes
HDU +1 | DER Unit #1 VArs Available that can be produced without impacting active power (Watts) output | 2 | -2147483648 | 2147483647 | 1 | 0 | VARs | (1%) | DINV |  | VArAvl | MV | DINV.VArAvl | VV13-14 | Yes | new
#REF! | DER Unit #1 Actual Apparent Power output as percentage of maximum apparent power (VAMax) | 2 | 0 | 1000 | 0.1 | 0 | Percent | 0.1 | DRCS |  | VAPct | MV | DRCS.VAPct |  | Yes | new
#REF! | DER Unit #1 Actual amount of charging as a percentage of maximum apparent charging power (VAChaMax) | 2 | 0 | 1000 | 0.1 | 0 | Percent | 0.1 | DRCS |  | VAChaPct | MV | DRCS.VAChaPct |  | Yes | new
HDU +2 | DER Unit #1 Nameplate rating. Energy storage capability expressed in am-hours. | [7 empty] | DRAT |  | Artg | ASG | DRAT.Artg |  | Yes |  | Remove amp-hour ratings
HDU +3 | DER Unit #1 Nameplate rating. Energy storage capability expressed in watt-hours. | [7 empty] | DRAT |  | CapWhRtg | ASG | DRAT.CapWhRtg |  | Yes
HDU +4 | DER Unit #1 Available Apparent Power (in kVAs) | 1 | -2147483648 | 2147483647 | 1 | 0 | kVA | 1 |  |  |  |  | . |  | Yes
HDU +5 | DER Unit #1 Maximum Apparent Power capability | 2 | 0 | 2147483647 | 1 | 0 | VA | (1%) | DRCT |  | VAMax | ASG | DRCT.VAMax | VV11-12 | Yes | New IEC 61850 name | Was Vamax
HDU +6 | DER Unit #1 Calculation Method for total apparent power calculation <0> Reserved <1> Vector <2> Arithmetic | 2 | 0 | 2 | 1 | 0 | n/a | 1 | DRCT |  | ClcTotVA | ENG | DRCT.ClcTotVA |  | Yes | new
HDU +7 | DER Unit #1 PV Present Indicator, Storage Present Indicator - enumerated: <0>Unknown, <1> mixed, <2>reciprocating engine <3> fuel cell <4> PV <5> combined heat and power <6> PV and battery storage, <7> Battery storage | 0 | 0 | 7 | 1 | 0 | None | 0 | 1 |  | DERtyp | DRCT | 1.DERtyp | ENG | Yes | 1 | Moved per item 73.
. . . | DER Unit #2 . . . . DER Unit #e-1 points | [11 empty] | . |  | Yes
HDU + duhai(e-1) | DER Unit #e Number of hours the DER has been connected to the power system | 3 | 0 | 2147483647 | 1 | 0 | Hours | 1 | DRCS |  | OpTmh | INS | DRCS.OpTmh |  | Yes
#REF! | DER Unit #e Operational time in seconds since commissioning | 3 | 0 | 2147483647 | 1 | 0 | Seconds | 1 | DPST |  | OpTms | INS | DPST.OpTms |  | Yes
HDU + duhai(e-1) )+1 | DER Unit #e VArs Available that can be produced without impacting active power (Watts) output | 2 | -2147483648 | 2147483647 | 1 | 0 | VARs | (1%) | DINV |  | VArAvl | MV | DINV.VArAvl | VV13-14 | Yes | new
#REF! | DER Unit #e Actual Apparent Power output as percentage of maximum apparent power | 2 | 0 | 1000 | 0.1 | 0 | Percent | 0.1 | DRCS |  | VAPct | MV | DRCS.VAPct |  | Yes | new
#REF! | DER Unt #e Actual amount of charging as a percentage of maximum apparent charging power | 2 | 0 | 1000 | 0.1 | 0 | Percent | 0.1 | DRCS |  | VAChaPct | MV | DRCS.VAChaPct |  | Yes | new
HDU + duhai(e-1) )+2 | DER Unit #e Nameplate rating. Energy storage capability expressed in amp-hours. | [7 empty] | DRAT |  | Artg | ASG | DRAT.Artg |  | Yes
HDU + duhai(e-1) )+3 | DER Unit #e Nameplate rating. Energy storage capability expressed in watt-hours. | [7 empty] | DRAT |  | WHRtg | ASG | DRAT.WHRtg |  | Yes
HDU + duhai(e-1) )+4 | DER Unit #e Available Apparent Power (in kVAs) | 1 | -2147483648 | 2147483647 | 1 | 0 | kVA | 1 |  |  |  |  | . |  | Yes
HDU + duhai(e-1) )+5 | DER Unit #e Maximum Apparent Power capability | 2 | 0 | 2147483647 | 1 | 0 | VA | (1%) | DRCT |  | VAMax | ASG | DRCT.VAMax | VV11-12 | Yes | New IEC 61850 name | Was Vamax
HDU + duhai(e-1) )+6 | DER Unit #e Calculation Method for total apparent power calculation | 2 | 0 | 2 | 1 | 0 | n/a | 1 | DRCT |  | ClcTotVA | ENG | DRCT.ClcTotVA |  | Yes | new
HDU + duhai(e-1) )+7 | DER Unit #e PV Present Indicator | 0 | 0 | 7 | 1 | 0 | None | 0 | 1 |  | DERtyp | DRCT | 1.DERtyp | ENG | Yes | 1 | Moved per item 73.
HI | Inverter #1 active power output - Present Active Power output level | 3 | -2147483648 | 2147483647 | 1 | 0 | Watts | 1 | MMXU |  | TotW | MV | MMXU.TotW |  | Yes
#REF! | Inverter #1 reactive output - Present reactive power output level | 3 | -2147483648 | 2147483647 | 1 | 0 | VARs | (1%) | MMXU |  | TotVAr | MV | MMXU.TotVAr |  | Yes
HI +1 | Inverer #1 DC input power | 3 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMDC |  | Watt | MV | MMDC.Watt |  | Yes
#REF! | Inverter #1 DC current level available to inverter | 3 | 0 | 2147483647 | 1 | 0 | Amp | (1%) | MMDC |  | Amp | MV | MMDC.Amp |  | Yes
#REF! | Inverter #1 DC voltage between PV system and inverter | 3 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMDC |  | Vol | MV | MMDC.Vol |  | Yes
HI +2 | Inverter #1 Active Power Target (in kW) | 1 | -2147483648 | 2147483647 | 1 | 0 | kW | 1 |  |  |  |  | . |  | Yes |  | These are settings for some of the functions. Why are they associated with the inverters?
HI +3 | Inverter #1 Reactive Power Target (in kVARs) | 1 | -2147483648 | 2147483647 | 1 | 0 | kVAR | 1 |  |  |  |  | . |  | Yes |  | These are settings for some of the functions. Why are they associated with the inverters?
HI +4 | Inverter #1 DC Voltage (in Volts) | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | 0.001 | MMDC |  | Vol | MV | MMDC.Vol |  | Yes
HI +5 | Inverter #1 DC Current (in Amps) | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | 0.1 | MMDC |  | Amp |  | MMDC.Amp |  | Yes
HI +6 | Inverter #1 AC Voltage (in Volts) | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | 0.1 | MMXU |  | PhV | Wye | MMXU.PhV |  | Yes
HI +7 | Inverter #1 AC Current (in Amps). | 1 | -2147483648 | 2147483647 | 0.001 | 0 | Amps | 0.001 | MMXU |  | A | WYE | MMXU.A |  | Yes
HI +8 | Inverter #1 Current Phase A (in Amps) | 1 | -2147483648 | 2147483647 | 0.001 | 0 | Amps | 0.001 | MMXU |  | A.phsA | WYE | MMXU.A.phsA |  | Yes
HI +9 | Inverter #1 Current Phase B (in Amps) | 1 | -2147483648 | 2147483647 | 0.001 | 0 | Amps | 0.001 | MMXU |  | A.phsB | WYE | MMXU.A.phsB |  | Yes
HI +10 | Inverter #1 Current Phase C (in Amps) | 1 | -2147483648 | 2147483647 | 0.001 | 0 | Amps | 0.001 | MMXU |  | A.phsC | WYE | MMXU.A.phsC |  | Yes
HI +11 | Inverter #1 Voltage Phase A to B (in Volts) | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | 0.001 | MMXU |  | V.phsAB | DEL | MMXU.V.phsAB |  | Yes
HI +12 | Inverter #1 Voltage Phase B to C (in Volts) | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | 0.001 | MMXU |  | V.phsBC | DEL | MMXU.V.phsBC |  | Yes
HI +13 | Inverter #1 Voltage Phase C to A (in Volts) | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | 0.001 | MMXU |  | V.phsCA | DEL | MMXU.V.phsCA |  | Yes
HI +14 | Inverter #1 Active Power (in kW) | 1 | -2147483648 | 2147483647 | 1 | 0 | kW | 1 |  |  |  |  | . |  | Yes |  | Not allowed in 61850
HI +16 | Inverter #1 Reactive Power (in kVARs) | 1 | -2147483648 | 2147483647 | 1 | 0 | kVAR | 1 |  |  |  |  | . |  | Yes |  | Not allowed in 61850
HI +15 | Inverter #1 Power Factor | 1 | -1 | 1 | 0.01 | 0 | N/A | 0.01 | MMXU |  | TotPF | MV | MMXU.TotPF |  | Yes
HI +17 | Inverter #1 Internal Temperature | 1 | -200 | 200 | 0.1 | 0 | Deg C | 0.1 | DINV |  | EnclTmp | MV | DINV.EnclTmp |  | Yes
HI +20 | Inverter #1 active power output - high threshold | 2 | 0 | 2147483647 | 1 | 0 | Watts | (1%) | MMXU |  | TotW.RangeC.hLim | MV | MMXU.TotW.RangeC.hLim |  | Yes | Fixed missing point index
HI +21 | Inverter #1 active power output - low threshold | 2 | 0 | 2147483647 | 1 | 0 | Watts | (1%) | MMXU |  | TotW.RangeC.lLim | MV | MMXU.TotW.RangeC.lLim |  | Yes
HI +19 | Inverter #1 reactive output – high threshold | 2 | 0 | 2147483647 | 1 | 0 | VARs | (1%) | MMXU |  | TotVAr.rangeC.hLim | MV | MMXU.TotVAr.rangeC.hLim |  | Yes
HI +22 | Inverter #1 reactive output – low threshold | 2 | 0 | 2147483647 | 1 | 0 | VARs | (1%) | MMXU |  | TotVAr.rangeC.lLim | MV | MMXU.TotVAr.rangeC.lLim |  | Yes
HI +23 | Inverter #1 Current output frequency – high threshold | 2 | 0 | 70000 | 1000 | 0 | Hz | 1 | MMXU |  | Hz.rangeC.hLim | MV | MMXU.Hz.rangeC.hLim |  | Yes
HI +24 | Inverter #1 Current output frequency – low threshold | 2 | 0 | 70000 | 1000 | 0 | Hz | 1 | MMXU |  | Hz.rangeC.lLim | MV | MMXU.Hz.rangeC.lLim |  | Yes
HI +25 | Inverter #1 DC Inverter input power - high threshold | 2 | 0 | 2147483647 | 1 | 0 | Watts | (1%) | MMDC |  | Watt.RangeC.hLim | MV | MMDC.Watt.RangeC.hLim |  | Yes
HI +16 | Inverter #1 DC Inverter input power - low threshold | 2 | 0 | 2147483647 | 1 | 0 | Watts | (1%) | MMDC |  | Watt.RangeC.lLim | MV | MMDC.Watt.RangeC.lLim |  | Yes
HI +15 | Inverter #1 DC input current available – high threshold | 2 | 0 | 2147483647 | 1 | 0 | Amps | (1%) | MMDC |  | Amp.RangeC.hLim | MV | MMDC.Amp.RangeC.hLim |  | Yes
HI +17 | Inverter #1 DC input current available – low threshold | 2 | 0 | 2147483647 | 1 | 0 | Amps | (1%) | MMDC |  | Amp.RangeC.lLim | MV | MMDC.Amp.RangeC.lLim |  | Yes
HI +20 | Inverter #1 DC voltage between DER system and inverter – high threshold | 2 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMDC |  | Vol.RangeC.hLim | MV | MMDC.Vol.RangeC.hLim |  | Yes |  | Changed per item #36
HI +21 | Inverter #1 DC voltage between DER system and inverter – low threshold | 2 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMDC |  | Vol.RangeC.lLim | MV | MMDC.Vol.RangeC.lLim |  | Yes |  | Changed per item #36
. . . | Inverter #2 . . . Inverter #p-1 points | [11 empty] | . |  | Yes
HI+ ihai(p-1) | Inverter #p active power output - | 3 | -2147483648 | 2147483647 | 1 | 0 | Watts | 1 | MMXU |  | TotW | MV | MMXU.TotW |  | Yes
#REF! | Inverter #p reactive output | 3 | -2147483648 | 2147483647 | 1 | 0 | VARs | (1%) | MMXU |  | TotVAr | MV | MMXU.TotVAr |  | Yes
HI+ ihai(p-1) +1 | Inverter #p DC Inverter input power | 3 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMDC |  | Watt | MV | MMDC.Watt |  | Yes
#REF! | Inverter #p DC current level available to inverter | 3 | 0 | 2147483647 | 1 | 0 | Amp | (1%) | MMDC |  | Amp | MV | MMDC.Amp |  | Yes
#REF! | Inverter #p DC voltage between PV system and inverter | 3 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMDC |  | Vol | MV | MMDC.Vol |  | Yes
HI+ ihai(p-1) +2 | Inverter #p Active Power Target (in kW) | 1 | -2147483648 | 2147483647 | 1 | 0 | kW | 1 |  |  |  |  | . |  | Yes
HI+ ihai(p-1) +3 | Inverter #p Reactive Power Target (in VARs) | 1 | -2147483648 | 2147483647 | 1 | 0 | kVAR | 1 |  |  |  |  | . |  | Yes
HI+ ihai(p-1) +4 | Inverter #p DC Voltage (in Volts) | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | 0.001 |  |  |  |  | . |  | Yes
HI+ ihai(p-1) +5 | Inverter #p DC Current (in Amps) | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | 0.1 |  |  |  |  | . |  | Yes
HI+ ihai(p-1) +6 | Inverter #p AC Voltage (in Volts) | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | 0.1 |  |  |  |  | . |  | Yes
HI+ ihai(p-1) +7 | Inverter #p AC Current (in Amps). | 1 | -2147483648 | 2147483647 | 0.001 | 0 | Amps | 0.001 |  |  |  |  | . |  | Yes
HI+ ihai(p-1) +8 | Inverter #p Current Phase A (in Amps) | 1 | -2147483648 | 2147483647 | 0.001 | 0 | Amps | 0.001 |  |  |  |  | . |  | Yes
HI+ ihai(p-1) +9 | Inverter #p Current Phase B (in Amps) | 1 | -2147483648 | 2147483647 | 0.001 | 0 | Amps | 0.001 |  |  |  |  | . |  | Yes
HI+ ihai(p-1) +10 | Inverter #p Current Phase C (in Amps) | 1 | -2147483648 | 2147483647 | 0.001 | 0 | Amps | 0.001 |  |  |  |  | . |  | Yes
HI+ ihai(p-1) +11 | Inverter #p Voltage Phase A to B (in Volts) | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | 0.001 |  |  |  |  | . |  | Yes
HI+ ihai(p-1) +12 | Inverter #p Voltage Phase B to C (in Volts) | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | 0.001 |  |  |  |  | . |  | Yes
HI+ ihai(p-1) +13 | Inverter #p Voltage Phase C to A (in Volts) | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | 0.001 |  |  |  |  | . |  | Yes
HI+ ihai(p-1) +14 | Inverter #p Active Power (Watts) | 1 | -2147483648 | 2147483647 | 1 | 0 | kW | 1 |  |  |  |  | . |  | Yes
HI+ ihai(p-1) +16 | Inverter #p Reactive Power (in VARs) | 1 | -2147483648 | 2147483647 | 1 | 0 | kVAR | 1 |  |  |  |  | . |  | Yes
HI+ ihai(p-1) +15 | Inverter #p Power Factor | 1 | -1 | 1 | 0.01 | 0 | N/A | 0.01 |  |  |  |  | . |  | Yes
HI+ ihai(p-1) +17 | Inverter #p Internal Temperature | 1 | -200 | 200 | 0.1 | 0 | Deg C | 0.1 |  |  |  |  | . |  | Yes
HI+ ihai(p-1) +20 | Inverter #p active power output - high threshold | 2 | 0 | 2147483647 | 1 | 0 | Watts | (1%) | MMXU |  | TotW | MV | MMXU.TotW |  | Yes
HI+ ihai(p-1) +21 | Inverter #p active power output - low threshold | 2 | 0 | 2147483647 | 1 | 0 | Watts | (1%) | MMXU |  | TotW | MV | MMXU.TotW |  | Yes
HI+ ihai(p-1) +19 | Inverter #p reactive output – high threshold | 2 | 0 | 2147483647 | 1 | 0 | VARs | (1%) | MMXU |  | TotVAr | MV | MMXU.TotVAr |  | Yes
HI+ ihai(p-1) +22 | Inverter #p reactive output – low threshold | 2 | 0 | 2147483647 | 1 | 0 | VARs | (1%) | MMXU |  | TotVAr | MV | MMXU.TotVAr |  | Yes
HI+ ihai(p-1) +23 | Inverter #p Current output frequency – high threshold | 2 | 0 | 70000 | 0.001 | 0 | Hz | 0.001 | MMXU |  | Hz | MV | MMXU.Hz |  | Yes
HI+ ihai(p-1) +24 | Inverter #p Current output frequency – low threshold | 2 | 0 | 70000 | 0.001 | 0 | Hz | 0.001 | MMXU |  | Hz | MV | MMXU.Hz |  | Yes
HI+ ihai(p-1) +25 | Inverter #p DC Inverter input power - high threshold | 2 | 0 | 2147483647 | 1 | 0 | Watts | (1%) | MMDC |  | Watt | MV | MMDC.Watt |  | Yes
HI+ ihai(p-1) +26 | Inverter #p DC Inverter input power - low threshold | 2 | 0 | 2147483647 | 1 | 0 | Watts | (1%) | MMDC |  | Watt | MV | MMDC.Watt |  | Yes
HI+ ihai(p-1) +27 | Inverter #p DC input current available – high threshold | 2 | 0 | 2147483647 | 1 | 0 | Amps | (1%) | MMDC |  | Amp | MV | MMDC.Amp |  | Yes
HI+ ihai(p-1) +28 | Inverter #p DC input current available – low threshold | 2 | 0 | 2147483647 | 1 | 0 | Amps | (1%) | MMDC |  | Amp | MV | MMDC.Amp |  | Yes
HI+ ihai(p-1) +29 | Inverter #p DC voltage between DER system and inverter – high threshold | 2 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMDC |  | Vol | MV | MMDC.Vol |  | Yes |  | Changed per item #36
HI+ ihai(p-1) +30 | Inverter #p DC voltage between DER system and inverter – low threshold | 2 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | MMDC |  | Vol | MV | MMDC.Vol |  | Yes |  | Changed per item #36
HB | External battery voltage (between battery charger and battery) | 3 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | DBAT |  | Vol | MV | DBAT.Vol |  | Yes
#REF! | Internal battery voltage | 3 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | DBAT |  | InBatV | MV | DBAT.InBatV |  | Yes
HB+1 | State of Charge – currently available energy in the battery, as a percentage of capacity rating | 3 | 0 | 1000 | 0.1 | 0 | Percent | 0.1 | DBAT |  | SocWh | ASG | DBAT.SocWh |  | Yes
#REF! | Battery Type of storage: <0> n/a, Unknown <1> Lead-acid <2> Nickel-metal hydrate (NiMH) <3> Nickel-cadmium (NiCad) <4> Lithium <5> Carbon zinc <6> Zinc chloride <7> Alkaline <8> Rechargeable alkaline <9> Sodium sulphur (NaS) <10> Flow <99> Other | 2 | 0 | 99 | 1 | 0 | None (list) | 1 | DBAT |  | BatTyp | ENG | DBAT.BatTyp | ZBAT | Yes | 1 | Battery point and moved from AO's per item 77.
#REF! | Battery #1 Setpoint for maximum State of Charge (percent full) | 2 | 0 | 1000 | 0.1 | 0 | Percent | 1 | DRCT |  | CapWhRtg | ASG | DRCT.CapWhRtg | INV4 | Yes | Battery level per item #89
HB+2 | Battery #1 Setpoint for Watt-hrs Capacity Rating - The useable capacity of the storage system in Watt-hrs. Use if BO Storage Limit Units is set to Watt-hrs. | 2 | 0 | 2147483647 | 1 | 0 | Watt-hrs | (1%) | DBAT |  | CapWhUseRtg | ASG | DBAT.CapWhUseRtg | INV4 | Yes | Battery level per item #89
HB+3 | Battery #1 Setpoint for Watt-hrs Storage Reserve. Use if BO Storage Limit Units is set to Watt-hrs | 2 | 0 | 2147483647 | 1 | 0 | Watt-hrs | (1%) | DBAT |  | CapUseRsvMax | ASG | DBAT.CapUseRsvMax | INV4 | Yes | Battery level per item #89
HB+4 | Battery #1 Setpoint for Amp-hrs Capacity Rating - The useable capacity of the battery in Amp-hrs. Use if BO Storage Limit Units is set to Amp-hrs. | 2 | 0 | 2147483647 | 1 | 0 | Amp-hrs | (1%) | DBAT |  | AhrRtg | ASG | DBAT.AhrRtg | INV4 |  | Battery level per item #89 | We agreed all capacities would be watt-hours - suggest we delete
HB+5 | Battery #1 Setpoint for Amp-hrs Storage Reserve. Use if BO Storage Limit Units is set to Amp-hrs. | 2 | 0 | 2147483647 | 1 | 0 | Amp-hrs | (1%) | DBAT |  | MinAhrRtg | ASG | DBAT.MinAhrRtg | INV4 |  | Battery level per item #89 | We agreed all capacities would be watt-hours - suggest we delete
HB+6 | Battery #1 Setpoint for minimum reserve for storage, as a percentage of the nominal maximum storage (DBAT.CapWhRtg) | 2 | 0 | 1000 | 0.1 | 0 | Percent | 1 | DBAT |  | CapUseRsvMin | ING | DBAT.CapUseRsvMin | INV4 | Yes | Battery level per item #89
HB+7 | Battery #1 Maximum charge voltage | 2 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | DBTC |  | ChaV.RangeC.hLim | ASG | DBTC.ChaV.RangeC.hLim | INV4 | Yes
HB+8 | Battery #1 External voltage (between battery charger and battery) – high threshold | 2 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | DBAT |  | HiBatVol | MV | DBAT.HiBatVol |  | Yes
HB+9 | Battery #1 External battery voltage (between battery charger and battery) – low threshold | 2 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | DBAT |  | LoBatVol | MV | DBAT.LoBatVol |  | Yes
HB+10 | Battery #1 Internal voltage – high threshold | 2 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | DBAT |  | InBatV.RangC.hLim | MV | DBAT.InBatV.RangC.hLim |  | Yes
HB+11 | Battery #1 Internal voltage – low threshold | 2 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | DBAT |  | InBatV.RangC.lLim | MV | DBAT.InBatV.RangC.lLim |  | Yes
HB+12 | Battery Bank #1 Battery State | 1 | 1 | 5 | 1 | 0 |  | 1 | DBAT |  | BatSt | SPS | DBAT.BatSt |  | Yes |  | This is a BO
HB+13 | Battery Bank #1 State of Charge (%) | 1 | 0 | 100 | 0.001 | 0 | Pct | 0.001 | DBAT |  | SocWh | MV | DBAT.SocWh |  | Yes
HB+14 | Battery Bank #1 State of Health (%) | 1 | 0 | 100 | 0.001 | 0 | Pct | 0.001 | DBAT |  | EEHealth | ENS | DBAT.EEHealth |  | Yes |  | This is not a percent, but an enumeration
HB+16 | Battery Bank #1 DC Bus Voltage (in Volts) | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | 0.001 | DBAT |  | IntnBatV | MV | DBAT.IntnBatV |  | Yes
HB+15 | Battery Bank #1 Current (in Amps) | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | 0.1 | DBAT |  | IntnBatA | MV | DBAT.IntnBatA |  | Yes
HB+17 | Battery Bank #1 Power (in kW) | 1 | -2147483648 | 2147483647 | 0.1 | 0 | kW | 0.1 |  |  |  |  | . |  | Yes
HB+20 | Battery Bank #1 Minimum Cell Voltage (in Volts) | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | 0.001 | DBAT |  | CelV.RangeC.lLim | MV | DBAT.CelV.RangeC.lLim |  | Yes
HB+21 | Battery Bank #1 Maximum Cell Voltage (in Volts) | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | 0.001 | DBAT |  | CelV.RangeC.hLim | MV | DBAT.CelV.RangeC.hLim |  | Yes
HB+19 | Battery Bank #1 Minimum Cell Temperature | 1 | -200 | 200 | 0.1 | 0 | Deg C | 0.1 | DBAT |  | CelTmp.RangeC.lLim | MV | DBAT.CelTmp.RangeC.lLim |  | Yes
HB+22 | Battery Bank #1 Maximum Cell Temperature | 1 | -200 | 200 | 0.1 | 0 | Deg C | 0.1 | DBAT |  | CelTmp.RangeC.hLim | MV | DBAT.CelTmp.RangeC.hLim |  | Yes
HB+23 | Battery Bank #1 Charge Current Limit (in Amps) | 1 | 0 | 2147483647 | 0.1 | 0 | Amps | 0.1 | DBTC |  | ChaA.RangeC.hLim | MV | DBTC.ChaA.RangeC.hLim |  | Yes
HB+24 | Battery Bank #1 Discharge Current Limit (in Amps) | 1 | 0 | 2147483647 | 0.1 | 0 | Amps | 0.1 | DBAT |  | Amp | MV | DBAT.Amp |  | Yes
HB+25 | Battery Bank #1 Maximum Voltage Limit (in Volts) | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | 0.001 | DBAT |  | BatVNom.RangeC.hLim | MV | DBAT.BatVNom.RangeC.hLim |  | Yes
HB+26 | Battery Bank #1 Minimum Voltage Limit (in Volts) | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | 0.001 | DBAT |  | BatVNom.RangeC.lLim | MV | DBAT.BatVNom.RangeC.lLim |  | Yes
HB+27 | Battery Bank #1 Connected String Count | 1 | 0 | 2147483647 | 1 | 0 | N/A | 1 | DBAT |  | BatSerCnt | ING | DBAT.BatSerCnt |  | Yes
HB+28 | Battery Bank #1 Outside Ambient Temperature | 1 | -200 | 200 | 0.1 | 0 | Deg C | 0.1 | MMET |  | EnvTmp | MV | MMET.EnvTmp |  | Yes
. . . | Battery Bank #2 . . . Battery Bank #b-1 points | [11 empty] | . |  | Yes
HB+ bhai(b-1) | Battery #b Setpoint for maximum State of Charge | 2 | 0 | 1000 | 0.1 | 0 | Percent | 1 | DRCT |  | ChaMaxPct | ASG | DRCT.ChaMaxPct | INV4 | Yes | Battery level per item #89
#REF! | Battery #b Setpoint for Watt-hrs Capacity Rating | 2 | 0 | 2147483647 | 1 | 0 | Watt-hrs | (1%) | DBAT |  | WhrRtg | ASG | DBAT.WhrRtg | INV4 | Yes | Battery level per item #89
HB+ bhai(b-1) +1 | Battery #b Setpoint for Watt-hrs Storage Reserve. | 2 | 0 | 2147483647 | 1 | 0 | Watt-hrs | (1%) | DBAT |  | MinWhrRtg | ASG | DBAT.MinWhrRtg | INV4 | Yes | Battery level per item #89
#REF! | Battery #b Setpoint for Amp-hrs Capacity Rating - | 2 | 0 | 2147483647 | 1 | 0 | Amp-hrs | (1%) | DBAT |  | AhrRtg | ASG | DBAT.AhrRtg | INV4 | Yes | Battery level per item #89
#REF! | Battery #b Setpoint for Amp-hrs Storage Reserve. | 2 | 0 | 2147483647 | 1 | 0 | Amp-hrs | (1%) | DBAT |  | MinAhrRtg | ASG | DBAT.MinAhrRtg | INV4 | Yes | Battery level per item #89
HB+ bhai(b-1) +2 | Battery #b Setpoint for minimum reserve for storage, | 2 | 0 | 1000 | 0.1 | 0 | Percent | 1 | DRCT |  | MinRsrvPct | ING | DRCT.MinRsrvPct | INV4 | Yes | Battery level per item #89
HB+ bhai(b-1) +3 | Battery #b Maximum charge voltage | 2 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | DBAT |  | MaxChaV | ASG | DBAT.MaxChaV | INV4 | Yes
HB+ bhai(b-1) +4 | Battery #b External voltage (between battery charger and battery) – high threshold | 2 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | DBAT |  | Vol | MV | DBAT.Vol |  | Yes
HB+ bhai(b-1) +5 | Battery #b External battery voltage (between battery charger and battery) – low threshold | 2 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | DBAT |  | Vol | MV | DBAT.Vol |  | Yes
HB+ bhai(b-1) +6 | Battery #b Internal voltage – high threshold | 2 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | DBAT |  | InBatV | MV | DBAT.InBatV |  | Yes
HB+ bhai(b-1) +7 | Battery #b Internal voltage – low threshold | 2 | 0 | 2147483647 | 1 | 0 | Volts | (1%) | DBAT |  | InBatV | MV | DBAT.InBatV |  | Yes
HB+ bhai(b-1) +8 | Battery Bank #b Battery State | 1 | 1 | 5 | 1 | 0 | N/A | 1 |  |  |  |  | . |  | Yes
HB+ bhai(b-1) +9 | Battery Bank #b State of Charge (%) | 1 | 0 | 100 | 0.001 | 0 | Pct | 0.001 |  |  |  |  | . |  | Yes
HB+ bhai(b-1) +10 | Battery Bank #b State of Health (%) | 1 | 0 | 100 | 0.001 | 0 | Pct | 0.001 |  |  |  |  | . |  | Yes
HB+ bhai(b-1) +11 | Battery Bank #b DC Bus Voltage (in Volts) | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | 0.001 |  |  |  |  | . |  | Yes
HB+ bhai(b-1) +12 | Battery Bank #b Current (in Amps) | 1 | -2147483648 | 2147483647 | 0.1 | 0 | Amps | 0.1 |  |  |  |  | . |  | Yes
HB+ bhai(b-1) +13 | Battery Bank #b Power (in kW) | 1 | -2147483648 | 2147483647 | 0.1 | 0 | kW | 0.1 |  |  |  |  | . |  | Yes
HB+ bhai(b-1) +14 | Battery Bank #b Minimum Cell Voltage (in Volts) | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | 0.001 |  |  |  |  | . |  | Yes
HB+ bhai(b-1) +16 | Battery Bank #b Maximum Cell Voltage (in Volts) | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | 0.001 |  |  |  |  | . |  | Yes
HB+ bhai(b-1) +15 | Battery Bank #b Minimum Cell Temperature | 1 | -200 | 200 | 0.1 | 0 | Deg C | 0.1 |  |  |  |  | . |  | Yes
HB+ bhai(b-1) +17 | Battery Bank #b Maximum Cell Temperature | 1 | -200 | 200 | 0.1 | 0 | Deg C | 0.1 |  |  |  |  | . |  | Yes
HB+ bhai(b-1) +20 | Battery Bank #b Charge Current Limit (in Amps) | 1 | 0 | 2147483647 | 0.1 | 0 | Amps | 0.1 |  |  |  |  | . |  | Yes
HB+ bhai(b-1) +21 | Battery Bank #b Discharge Current Limit (in Amps) | 1 | 0 | 2147483647 | 0.1 | 0 | Amps | 0.1 |  |  |  |  | . |  | Yes
HB+ bhai(b-1) +19 | Battery Bank #b Maximum Voltage Limit (in Volts) | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | 0.001 |  |  |  |  | . |  | Yes
HB+ bhai(b-1) +22 | Battery Bank #b Minimum Voltage Limit (in Volts) | 1 | 0 | 2147483647 | 0.001 | 0 | Volts | 0.001 |  |  |  |  | . |  | Yes
HB+ bhai(b-1) +23 | Battery Bank #b Connected String Count | 1 | 0 | 2147483647 | 1 | 0 | N/A | 1 |  |  |  |  | . |  | Yes
HB+ bhai(b-1) +24 | Battery Bank #b Outside Ambient Temperature | 1 | -200 | 200 | 0.1 | 0 | Deg C | 0.1 |  |  |  |  | . |  | Yes

## AO
Point Index | Name/Description | Select/Operate | Direct Operate | Direct Operate – No Ack | Transmitted Value Minimum | Transmitted Value Maximum | Scaling Multiplier | OffSet | Units | Reso­-lution | Default Event Class - Chg | Default Event Class - Cmd | LN Class | LN Inst | Data Object | CDC | Unique String | Function | Part of Settings Group | MESA-ESS | Note 1 | Note 2
#REF! | Reference Voltage | X | X | X | 0 | 2147483647 | 1 | 0 | Volts | (1%) | 2 | 2 | DRCT |  | Vref | ASG | DRCT.Vref | VV11-14 |  | Yes
AO0 | Reference Voltage Offset | X | X | X | 0 | 2147483647 | 1 | 0 | Volts | (1%) | 2 | 2 | DRCT |  | VrefOfs | ASG | DRCT.VrefOfs | VV11-14 |  | Yes
#REF! | Reference for Reactive Power Setpoints. Selects which setpoint is active. Default is <3>. Also specifies whether Watts or VARs take precedence when providing reactive current support. If set to <3>, generating Watts has precedence. At any other setting, reactive current has precedence. <0> Not applicable / Unknown <1> Percent of Maximum Active Power (WMax) <2> Percent of Maximum Reactive Power (VArMax) <3> Percent of Available Reactive Power (VArAval) | X | X | X | 0 | 3 | 1 | 0 | n/a | 1 | 2 | 2 | DRCT |  | VArRef | ENG | DRCT.VArRef | VV13-14, TV31 |  |  | new | This should be set by the individual functions, not globally
#REF! | DER Start Time Window | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DOPM |  | WinTms | ING | DOPM .WinTms | INV1 |  |  |  | Per item 65
AO1 | DER Start Ramp Up Rate | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DOPM |  | RvrtTms |  | DOPM.RvrtTms |  |  |  | New | Per item 65, and item 70
AO2 | DER Stop (Cease to Energize)Time Window | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DCTE |  | WinTms | ING | DCTE.WinTms | INV1 |  |  |  | Per item 65
AO3 | DER Stop (Cease to Energize) Ramp Down rate | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DCTE |  | RvrtTms | ING | DCTE.RvrtTms | INV1 |  |  |  | Per item 65
AO4 | DER Stop Ramp Down Time | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DOPM |  | RvrtTms |  | DOPM.RvrtTms |  |  |  | New | Per item 65, and item 70
AO5 | Connect/Disconnect Time Window | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DOPM |  | WinTms | ING | DOPM .WinTms | INV1 |  |  |  | Per item 65
AO6 | Connect/Disconnect Reversion Timeout Period . Timeout (reversion time is for the Disconnect only) | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DOPM |  | RvrtTms | ING | #REF! | INV1 |  |  |  | Per item 65
AO7 | Setpoint for Nominal Frequency | X | X | X | 0 | 70000 | 0.001 | 0 | Hz | 0.001 | 2 | 2 | DOPR |  | ECPNomHz | ASG | #REF! | FW22 |  | Yes | Frequency scaling is .001 Hz per item #69
AO8 | Generation Ramp Up Rate. Percentage of Maximum Generation Rate (WMax) that the generation rate can change per minute when ramping up. | X | X | X | 0 | 1000 | 0.1 | 0 | Percent per min | 1 | 2 | 2 | DRCT |  | RmpUpRte | ASG | DRCT.RmpUpRte | INV2 |  |  | New IEC 61850 name and CDC. | One section of 90-7 (6.1.4) says per second, not per minute.
AO9 | Generation Ramp Down Rate. Percentage of Maximum Generation Rate (Wmax) that the generation rate can change per minute when ramping down. | X | X | X | 0 | 1000 | 0.1 | 0 | Percent per min | 1 | 2 | 2 | DRCT |  | RmpDnRte | ASG | DRCT1.RmpDnRte | INV2 |  |  | New IEC 61850 name and CDC. | One section of 90-7 (6.1.4) says per second, not per minute.
AO10 | Charging Ramp Up Rate. Percentage of Maximum Charging Rate (WChaMax) that the charging rate can change per minute when ramping up. | X | X | X | 0 | 1000 | 0.1 | 0 | Percent per min | 1 | 2 | 2 | DRCT | 1 | RmpUpRteCha | ING | DRCT1.RmpUpRteCha | ? |  |  | new | Don't understand this one at all. What does it reference?
AO11 | Charging Ramp Down Rate. Percentage of Maximum Charging Rate (WChaMax) that the charging rate can change per minute when ramping down. | X | X | X | 0 | 1000 | 0.1 | 0 | Percent per min | 1 | 2 | 2 | DRCT | 1 | RmpDnRteCha | ING | DRCT1.RmpDnRteCha | ? |  |  | new | Don't understand this one at all. What does it reference?
AO12 | Requested Settings Group <0> Not Used <1> Unspecified / Autonomously Determined (see BO Enable Sensed Grid Config Detection) <2> Factory Configuration <3> Default Configuration / Comms Lost <4> Normal Grid-Connected Configuration <5> Islanded Condition 1 (small, local island) <6> Islanded Condition 2 (larger, area island) <7> Islanded Condition 3 (largest, regional island) <8> 1st Alternate Grid-Connected Configuration <9> 2nd Alternate Grid-Connected Configuration <10> 3rd Alternate Grid-Connected Configuration <11-255> Reserved for future assignment | X | X | X | DCTE | 10 | 1 | 0 | n/a | 1 | 2 | 2 | DRCC | 1 | GridCfgSel | ENG | DRCC1.GridCfgSel | GCF | No |  | new | Proposed
AO13 | Settings Group Being Edited <0> Not Used <1> Unspecified / Autonomously Determined (see BO Enable Sensed Grid Config Detection) <2> Factory Configuration <3> Default Configuration / Comms Lost <4> Normal Grid-Connected Configuration <5> Islanded Condition 1 (small, local island) <6> Islanded Condition 2 (larger, area island) <7> Islanded Condition 3 (largest, regional island) <8> 1st Alternate Grid-Connected Configuration <9> 2nd Alternate Grid-Connected Configuration <10> 3rd Alternate Grid-Connected Configuration <11-255> Reserved for future assignment | X | X | X | 0 | 10 | 1 | 0 | n/a | 1 | 2 | 2 | DRCC | 1 | GridCfgEdt | ENG | DRCC.GridCfgEdt | GCF | No |  | new | Proposed
AO14 | Freeze Counter Interval. Interval between freeze counter operations after the initial occurrence. A zero value means the free counter operation is not repeated. | X | X | X | 0 | 2147483647 | 1 | 0 | N/A | 1 | 2 | 2 |  |  |  |  | . |  |  |  | New, from MESA set of DNP3 points
AO15 | Freeze Counter Interval Units. Units of the interval between freeze counter operations: <0> The outstation does not repeat the action, regardless of the Interval count. <1> Milliseconds - In this case the interval is always counted relative to the Start Time and is constant regardless of the clock time set at the Outstation. <2> Seconds - At the same millisecond within the second that is specified in the Start Time. <3> Minutes - At the same second and millisecond within the minute that is+C1 specified in the Start Time. <4> Hours - At the same minute, second and B7millisecond within the hour that is specified in the Start Time. <5> Days - At the same time of day that is specified in the Start Time. <6> Weeks - On the same day of the week at the same time of day that is specified in the Start Time <7> Months - On the same day of each month at the same time of day that is specified in the Start Time. If the Start Time falls on the 29th or greater day of the month, the outstation shall not perform the action in months that do not have such a day <8> Months on Same Day of Week from Start of Month - At the same time of day on the same day of the week after the beginning of the month as the day specified in the Start Time. For instance, if the Start Time specifies the second Tuesday of February and the Interval Count is 2, the next action shall occur on the second Tuesday of April. In the same example, if the Interval Count is set to 12, this is the same as specifying, “Every year on the second Tuesday in February”. If the specified day does not occur in a given month when an action was scheduled to occur, the outstation shall not perform the action that month but shall perform it at the next valid scheduled time. <9> Months on Same Day of Week from End of Month - The outstation shall interpret this setting as in <8>, but the day of the week shall be measured from the end of the month, e.g.,“the second-last Tuesday in February”. | X | X | X | 0 | 9 | 1 | 0 | N/A | 1 | 2 | 2 |  |  |  |  | 1. |  |  |  | New, from MESA set of DNP3 points
AO16 | Low/High Voltage Ride-Through Signal Meter ID. Referenced ECP. This is the meter from which current is being read to evaluate and provide support.
AO17 | Low/High Voltage Ride-Through High Must Trip Curve Index. Index of the Voltage Ride-through curve which specifies trip points when the voltage is high.
AO18 | Low/High Voltage Ride-Through Low Must Trip Curve Index. Index of the Voltage Ride-through curve which specifies trip points when the voltage is low.
AO19 | Low/High Frequency Ride-Through Signal Meter ID. Referenced ECP. This is the meter from which current is being read to evaluate and provide support.
AO20 | Low/High Frequency Ride-Through High Must Trip Curve Index. Index of the Frequency Ride-through curve which specifies trip points when the frequency is high.
AO21 | Low/High Frequency Ride-Through Low Must Trip Curve Index. Index of the Frequency Ride-through curve which specifies trip points when the frequency is low.
AO22 | Dynamic Reactive Current Support - Gradient Mode. <0> Undefined <1> Gradients reach 0 at the moving average Voltage <2> Gradients reach 0 at the Voltage deadbands | X | X | X | 0 | 2 | 1 | 0 | n/a | 1 | 2 | 2 | RDGS | 1 | ArGraMod | ENG | RDGS1.ArGraMod | TV31 |  | Yes
AO23 | Dynamic Reactive Current Support Deadband Minimum Voltage. Percentage of the nominal voltage (DRCT.Vref), measured from the moving average voltage (RDGS.VAv). Support is no longer applied when the voltage stays above this value for the length of the Hold Time. | X | X | X | 0 | 1000 | 0.1 | 0 | Percent | 1 | 2 | 2 | RDGS | 1 | DbVMin | ASG | RDGS1.DbVMin | TV31 |  | Yes
AO24 | Dynamic Reactive Current Support Deadband Maximum Voltage when applying reactive current support. Percentage of the nominal voltage (DRCT.Vref), measured from the moving average voltage (RDGS.VAv). Support is no longer applied when the voltage stays below this value for the length of the Hold Time. | X | X | X | 0 | 1000 | 0.1 | 0 | DCTE | 1 | 2 | 2 | RDGS | 1 | DbVMax | ASG | RDGS1.DbVMax | TV31 |  | Yes
AO25 | Dynamic Reactive Current Support Gradient for Sags. This is the percentage of the rated current (DRAT.ARtg) to apply capacitively per percentage of the negative deviation from the moving average voltage (RDGS.Av). It is a ratio of percent and is therefore unitless. | X | X | X | -2147483648 | 2147483647 | 0.001 | 0 | DCTE | 1 | 2 | 2 | RDGS | 1 | ArGraSag | ASG | RDGS1.ArGraSag | TV31 |  | Yes
AO26 | Dynamic Reactive Current Support Gradient for Swells . Percentage of the rated current (DRAT.ARtg) to apply inductively per percentage of the positive deviation from the moving average voltage (RDGS.Av). It is a ratio of percent and is therefore unitless. | X | X | X | -2147483648 | 2147483647 | 0.001 | 0 | n/a | 1 | 2 | 2 | RDGS | 1 | ArGraSwell | ASG | RDGS1.ArGraSwell | TV31 |  | Yes
AO27 | Dynamic Reactive Current Support Filter Time for Moving Average Voltage (RDGS.VAv) used to determine amount of dynamic reactive current support | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | RDGS | 1 | FiltTms | ING | RDGS1.FiltTms | TV31 |  | Yes
AO28 | Dynamic Reactive Current Support Block Zone Voltage.Percentage of the nominal voltage (DRCT.VRef) below which no reactive current support shall be applied. | X | X | X | 0 | 1000 | 0.1 | 0 | Percent | 1 | 2 | 2 | RDGS | 1 | BlkZnV | ASG | RDGS1.BlkZnV | TV31 |  | Yes
AO29 | Dynamic Reactive Current Support Hysteresis Block Zone Voltage for applying dynamic reactive current support. This is a percentage of the nominal voltage (DRCT.VRef). After being blocked, reactive current support shall not resume until the voltage has been above BlkZnV + HysBlkZnV. | X | X | X | 0 | 1000 | 0.1 | 0 | Percent | 1 | 2 | 2 | RDGS | 1 | HysBlkZnV | ASG | RDGS1.HysBlkZnV | TV31 |  | Yes
AO30 | Dynamic Reactive Current Support Block Zone Time. Time in milliseconds from the beginning of any "sag" event, before which dynamic reactive current support will always continue, regardless of how low voltage may sag. | X | X | X | 0 | 2147483647 | 1 | 0 | ms | 1 | 2 | 2 | RDGS | 1 | BlkZnTmms | ING | RDGS1.BlkZnTmms | TV31 |  | Yes
AO31 | Dynamic Reactive Current Support Hold Time. When the voltage returns to within the deadband limits (RDGS.dbVMin annd RDGS.dbVMax) for this length of time (measured in milliseconds), the "sag" or "swell" event is considered to be over. Reactive current support ends, frozen values are unfrozen, and a new event can begin. | X | X | X | 0 | 2147483647 | 1 | 0 | ms | 1 | 2 | 2 | RDGS | 1 | HoldTmms | ING | RDGS.HoldTmms | TV31 |  | Yes
AO32 | Dynamic Reactive Current Support Time Window | X | X | X | 1 | 0 | 1 | 0 | Sec | 1 | [6 empty] | . |  |  | Yes
AO33 | Dynamic Reactive Current Support Timeout Period | X | X | X | 1 | 0 | 1 | 0 | Sec | 1 | [6 empty] | . |  |  | Yes
AO34 | Dynamic Reactive Current Support Ramp Up Time | X | X | X | 1 | 0 | 1 | 0 | Sec | 1 | [6 empty] | . |  |  | Yes
AO35 | Dynamic Reactive Current Support Ramp Down Time | X | X | X | 1 | 0 | 1 | 0 | Sec | 1 | [6 empty] | . |  |  | Yes
AO36 | Dynamic Reactive Current Support Mode Priority | X | X | X | 0 | number of modes | 1 | 0 | n/a | 1 | [6 empty] | . |  |  | Yes
AO37 | Dynamic Volt-Watt Gradient. Signed unit-less quantity that establishes the ratio of additional Watts supplied (expressed in terms of % DRCT.WMax) to the present difference from the moving average voltage (expressed as % DRCT.VRef). | X | X | X | -2147483648 | 2147483647 | 0.001 | 0 | n/a | 1 | 2 | 2 | DRCT | 1 | DynVWGra | ASG | DRCT1.DynVWGra | DVW |  | Yes
AO38 | Dynamic Volt-Watt Filter Time. The time in seconds used to calculate the moving average voltage for dynamic Volt-Watt support. | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DRCT | 1 | VWFilTms | ASG | DRCT1.VWFilTms | DVW |  | Yes
AO39 | Dynamic Volt-Watt Lower Deadband. Percentage of the nominal voltage (DRCT.Vref) measured below the moving average voltage. If the present voltage is above this value, no additional Watts shall be supplied. | X | X | X | 0 | 1000 | 0.1 | 0 | Volts | 1 | 2 | 2 | DRCT | 1 | DbVWLo | ASG | DRCT1.DbVWLo | DVW |  | Yes
AO40 | Dynamic Volt-Watt Upper Deadband. Percentage of the nominal voltage (DRCT.Vref) measured above the moving average voltage. If the present voltage is below this value, no additional Watts shall be supplied. | X | X | X | 0 | 1000 | 0.1 | 0 | Volts | 1 | 2 | 2 | DRCT | 1 | DbVWHi | ASG | DRCT8.DbVWHi | DVW |  | Yes
AO41 | Dynamic Volt-Watt Timeout period | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DOPM | 8 | RvrtTms | ING | DOPM.RvrtTms | DVW |  | Yes
AO42 | Dynamic Volt-Watt Mode Priority | X | X | X | 0 | number of modes | 1 | 0 | n/a | 1 | [6 empty] | . |  |  | Yes
AO43 | Freq-Watt Emergency Signal Meter ID | X | X | X | 0 | 2147483647 | 1 | 0 |  | 1 | 2 | 2 |  |  |  |  | . |  |  | Yes
AO44 | Freq-Watt Emergency Target Frequency | X | X | X | 0 | 2147483647 | 0.01 | 0 | Hertz | 0.01 | 2 | 2 |  |  |  |  | . |  |  | Yes
AO45 | Freq-Watt Emergency Lower Outer Limit | X | X | X | 0 | 2147483647 | 0.001 | 0 | Hertz | 0.001 | 2 | 2 |  |  |  |  | . |  |  | Yes
AO46 | Freq-Watt Emergency Lower Inner Limit | X | X | X | 0 | 2147483647 | 0.001 | 0 | Hertz | 0.001 | 2 | 2 |  |  |  |  | . |  |  | Yes
AO47 | Freq-Watt Emergency Upper Outer Limit | X | X | X | 0 | 2147483647 | 0.001 | 0 | Hertz | 0.001 | 2 | 2 |  |  |  |  | . |  |  | Yes
AO48 | Freq-Watt Emergency Upper Inner Limit | X | X | X | 0 | 2147483647 | 0.001 | 0 | Hertz | 0.001 | 2 | 2 |  |  |  |  | . |  |  | Yes
AO49 | Freq-Watt Emergency Violation Response Delay | X | X | X | 0 | 2147483647 | 1 | 0 | MS | 1 | 2 | 2 |  |  |  |  | . |  |  | Yes
AO50 | Freq-Watt Emergency Healthy Response Delay | X | X | X | 0 | 2147483647 | 1 | 0 | MS | 1 | 2 | 2 |  |  |  |  | 1. |  |  | Yes
AO51 | Freq-Watt Emergency SoC Target | X | X | X | 0 | 1000 | 0.1 | 0 | Percent | 0.1 | 2 | 2 | DRCT | 1 | WMaxLimPct |  | DRCT.WMaxLimPct |  |  | Yes
AO52 | Freq-Watt Emergency SoC Restoration Rate | X | X | X | 0 | 2147483647 | 1 | 0 | kW | 1 | 2 | 2 |  |  |  |  | . |  |  | Yes
AO53 | Freq-Watt Emergency Time Window | X | X | X | 0 | 2147483647 | 1 | 0 | Sec | 1 | 2 | 2 |  |  |  |  | . |  |  | Yes
AO54 | Freq-Watt Emergency Timeout Period | X | X | X | 0 | 2147483647 | 1 | 0 | Sec | 1 | 2 | 2 |  |  |  |  | . |  |  | Yes
AO55 | Freq-Watt Emergency Ramp Up Time | X | X | X | 0 | 2147483647 | 1 | 0 | Sec | 1 | 2 | 2 |  |  |  |  | . |  |  | Yes
AO56 | Freq-Watt Emergency Ramp Down Time | X | X | X | 0 | 2147483647 | 1 | 0 | Sec | 1 | 2 | 2 |  |  |  |  | . |  |  | Yes
AO57 | Freq-Watt Emergency Mode Priority | X | X | X | 0 | number of modes | 1 | 0 | n/a | 1 | [6 empty] | . |  |  | Yes
AO58 | Active Power Limit Charge Setpoint. Maximum allowed Watts as a percentage of Maximum Active Power capability, | X | X | X | 0 | 1000 | 0.1 | 0 | Percent | 0.1 | 2 | 2 | DRCT | 1 | WMaxLimPct |  | DRCT1.WMaxLimPct |  |  | Yes | New | Per item 67
AO59 | Active Power Limit Discharge Setpoint. Maximum allowed Watts as a percentage of Maximum Active Power capability, | X | X | X | 0 | 1000 | 0.1 | 0 | Percent | 1 | 2 | 2 | DRCT | 1 | WMaxLimPct | ING | DRCT2.WMaxLimPct | INV2 |  | Yes | New | Per item 67
AO60 | Active Power Limit Time Window | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DOPM | 2 | RvrtTms | ING | DOPM2.RvrtTms | INV2 |  | Yes
AO61 | Active Power Limit Timeout Period | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DOPM | 2 |  |  | DOPM2. |  |  | Yes
AO62 | Active Power Limit Ramp Up Time | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DOPM | 2 | RmpTms | ING | DOPM2.RmpTms | INV2 |  | Yes
AO63 | Active Power Limit Ramp Down Time | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DOPM | 2 | RmpTms | ING | DOPM.RmpTms | INV2 |  | Yes
AO64 | Active Power Limit Priority | X | X | X | 0 | number of modes | 1 | 0 | n/a | 1 | [6 empty] | 1. |  |  | Yes
AO65 | Charge/Discharge Active Power Target Percentage of maxmum charge/discharge rate | X | X | X | -1000 | 1000 | 1 | 0 | % | 0.1 | 2 | 2 | DCHD |  | WTgt | ASG | DCHD.WTgt | INV4 |  | Yes
AO66 | Charge/Discharge Time Window | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DCHD |  | WinTms | ING | DCHD.WinTms | INV4 |  | Yes
AO67 | Charge/Discharge Ramp Time | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DCHD |  | RmpTms | ING | DCHD.RmpTms | INV4 |  | Yes
AO68 | Charge/Discharge Timeout Period | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DCHD |  | RevtTms | ING | DCHD.RevtTms | INV4 |  | Yes
AO69 | Charge/Discharge Discharge Ramp Up Time | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DCHD |  | RmpUpRte | ING | DCHD.RmpUpRte | INV4 |  | Yes
AO70 | Charge/Discharge Discharge Ramp Down Time | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DCHD |  | RmpDnRte | ING | DCHD.RmpDnRte | INV4 |  | Yes
AO71 | Charge/Discharge Charge Ramp Up Time | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DCHD |  | ChaRmpUpRte | ING | DCHD.ChaRmpUpRte | INV4 |  | Yes
AO72 | Charge/Discharge Charge Ramp Down Time | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DCHD |  | ChaRmpDnRte | ING | DCHD.ChaRmpDnRte | INV4 |  | Yes
AO73 | Charge/Discharge VAr Action to take when switching between charging and discharging: <0> Reserved <1> Reverse producing/absorbing Vars when changing betweeen charging and discharging (go to diagonal quadrant Q1/Q3 or Q2/Q4) <2> Do not reverse producing/absorbing Vars (go to adjacent quadrant Q1/Q2 or Q3/Q4) | X | X | X | 0 | 2 | 1 | 0 | n/a | 1 | 2 | 2 | DRCT | 1 | VArAct | ENG | DRCT.VArAct | INV3 |  | Yes | In the basic profile <1> was the only value permitted. | Default is <1>.
AO74 | Charge/Discharge Minimum Reserve for Storage: The minimum level to which the storage system may be discharged, expressed as a percentage of the total usable storage. |  |  |  | -1000 | 1000 | 1 | 0 | Percent | 0.1 | [6 empty] | . |  |  | Yes
AO75 | Charge/Discharge Maximum Reserve for Storage: The maximum level to which the storage system may be discharged, expressed as a percentage of the total usable storage. |  |  |  | -1000 | 1000 | 1 | 0 | Percent | 0.1 | [6 empty] | . |  |  | Yes
AO76 | Charge/Discharge Target State of Charge. Charge that the system is expected to achieve, as a percentage of the usable capacity. |  |  |  | 0 | 1000 | 0.1 | 0 | Percent | 0.1 | [6 empty] | . |  |  | Yes
AO77 | Charge/Discharge Time Charge Needed. time by which the storage system must reach the target SOC |  |  |  | 0 | 2147483647 | 1 | 0 | Seconds | [7 empty] | . |  |  | Yes
AO78 | Charge/Discharge Mode Priority | X | X | X | 0 | number of modes | 1 | 0 | n/a | 1 | [6 empty] | 1. |  |  | Yes
AO79 | Peak Power Limiting Power Limit. Target value of the reference load power (MMXN2.Watt). The inverter shall discharge Watts to ensure the reference load does not exceed this limit. | X | X | X | 0 | 1000 | 0.1 | 0 | Percent | 0.1 | 2 | 2 | DRCT | 1 | WMaxLimPct, DRCT.PkWLim |  | DRCT.WMaxLimPct, DRCT.PkWLim |  |  | Yes
AO80 | Peak Power Limiting Signal Meter ID | 2 | 0 | 2147483647 | 1 | 0 |  | 1 | [8 empty] | 1. |  |  | Yes
AO81 | Peak Power Limit. This is the target value of the reference load power (MMXN2.Watt). The inverter shall discharge Watts to ensure the reference load does not exceed this limit. | X | X | X | 0 | 2147483647 | 1 | 0 | Watts | 1 | 2 | 2 | DRCT | 1 | DRCT.PkWLim | ASG | DRCT9.DRCT.PkWLim | PPL |  | Yes
AO82 | Peak Power Limiting Time Window | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DOPM | 9 | WinTms | ING | DOPM9.WinTms | PPL |  | Yes
AO83 | Peak Power Limiting Timeout Period | X | X | X | 0 | 2147483647 | 1 | 0 | Sec | 1 | 2 | 2 | DOPM | 9 | RvrtTms | ING | DOPM.RvrtTms | PPL |  | Yes
AO84 | Peak Power Limiting Ramp Up Time | X | X | X | 0 | 2147483647 | 1 | 0 | Sec | 1 | 2 | 2 |  |  | DOPM | 9 | 9.DOPM | RmpTms | ING | Yes
AO85 | Peak Power Limiting Ramp Down Time | X | X | X | 0 | 2147483647 | 1 | 0 | Sec | 1 | 2 | 2 | DOPM | 9 | RmpTms | ING | DOPM.RmpTms |  |  | Yes
AO86 | Peak Power Limiting Mode Priority | X | X | X | 0 | number of modes | 1 | 0 | n/a | 1 | [6 empty] | . |  |  | Yes
AO87 | Load Following Signal Meter ID | X | X | X | 2147483647 | 1 | 0 |  | N/A | 1 | [6 empty] | . |  |  | Yes
AO88 | Load Following Ratio | X | X | X | 100 | 0.001 | 0 |  | N/A | 0.001 | [6 empty] | #REF! |  |  | Yes
AO89 | Load Starting Threshold. If this power power level is not exceeded (in absolute value), load following does not occur. Expressed in Watts. The Starting Watt Threshold may be set to zero. Positive value for load. | X | X | X | 0 | 1000 | 0.1 | 0 | Percent | 1 | 2 | 2 | DRCT | 1 | WFolRat | ASG | DRCT.WFolRat | LGF |  | Yes
AO90 | Load Following Time Window | X | X | X | 2147483647 | 1 | 0 |  | Sec | 1 | [6 empty] | 10. |  |  | Yes
AO91 | Load Following Timeout Period | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DOPM | 10 | RvrtTms | ING | DOPM10.RvrtTms | LGF |  | Yes
AO92 | Load Following Ramp Up Time | X | X | X | 2147483647 | 1 | 0 |  | Seconds | 1 | 2 | 2 | DOPM | 10 | RmpTms | ING | DOPM10.RmpTms | LGF |  | Yes
AO93 | Load Following Ramp Down Time | X | X | X | 2147483647 | 1 | 0 |  | Seconds | 1 | 2 | 2 | DOPM | 10 | RmpTms | ING | DOPM.RmpTms | LGF |  | Yes
AO94 | Load Following Mode Priority | X | X | X | 0 | number of modes | 1 | 0 | n/a | 1 | [6 empty] | . |  |  | Yes
AO95 | Generation Following Signal Meter ID | X | X | X | 2147483647 | 1 | 0 |  | N/A | 1 | [6 empty] | . |  |  | Yes
AO96 | Generation Following Ratio | X | X | X | 100 | 0.001 | 0 |  | N/A | 0.001 | [6 empty] | #REF! |  |  | Yes
AO97 | Generation Starting Threshold. If this power power level is not exceeded (in absolute value), generation following does not occur. Expressed in Watts. The Starting Watt Threshold may be set to zero. Negative value for generation. | X | X | X | 0 | 1000 | 0.1 | 0 | Percent | 1 | 2 | 2 | DRCT | 1 | WFolRat | ASG | DRCT.WFolRat | LGF |  | Yes
AO98 | Generation Following Time Window | X | X | X | 2147483647 | 1 | 0 |  | Sec | 1 | [6 empty] | 10. |  |  | Yes
AO99 | Generation Following Timeout Period | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DOPM | 10 | RvrtTms | ING | DOPM10.RvrtTms | LGF |  | Yes
AO100 | Generation Following Ramp Up Time | X | X | X | 2147483647 | 1 | 0 |  | Seconds | 1 | 2 | 2 | DOPM | 10 | RmpTms | ING | DOPM10.RmpTms | LGF |  | Yes
AO101 | Generation Following Ramp Down Time | X | X | X | 2147483647 | 1 | 0 |  | Seconds | 1 | 2 | 2 | DOPM | 10 | RmpTms | ING | DOPM.RmpTms | LGF |  | Yes
AO102 | Generation Following Mode Priority | X | X | X | 0 | number of modes | 1 | 0 | n/a | 1 | [6 empty] | 7. |  |  | Yes
AO103 | AGC Signal Value | X | X | X | 1 | 0.001 | 0 |  | Per Unit | 0.001 | [6 empty] | . |  |  | Yes
AO104 | AGC Signal Interval | X | X | X | 2147483647 | 1 | 0 |  | Sec | 1 | [6 empty] | . |  |  | Yes
AO105 | AGC Minimum Average SOC | X | X | X | 100 | 0.001 | 0 |  | Pct | 0.001 | [6 empty] | . |  |  | Yes
AO106 | AGC Maximum Average SOC | X | X | X | 100 | 0.001 | 0 |  | Pct | 0.001 | [6 empty] | . |  |  | Yes
AO107 | AGC Time Window | X | X | X | 2147483647 | 1 | 0 |  | Sec | 1 | [6 empty] | . |  |  | Yes
AO108 | AGC Timeout Period | X | X | X | 2147483647 | 1 | 0 |  | Sec | 1 | [6 empty] | . |  |  | Yes
AO109 | AGC Ramp Up Time | X | X | X | 2147483647 | 1 | 0 |  | Sec | 1 | [6 empty] | . |  |  | Yes
AO110 | AGC Timeout Period | X | X | X | 2147483647 | 1 | 0 |  | Sec | 1 | [6 empty] | . |  |  | Yes
AO111 | AGC Ramp Down Time | X | X | X | 2147483647 | 1 | 0 |  | Sec | 1 | [6 empty] | . |  |  | Yes
AO112 | AGC Mode Priority | X | X | X | 0 | number of modes | 1 | 0 | n/a | 1 | [6 empty] | . |  |  | Yes
AO113 | Active Power Smoothing Signal Meter ID | X | X | X | 2147483647 | 1 | 0 |  | N/A | 1 | [6 empty] | . |  |  | Yes
AO114 | Active Power Smoothing Lower Limit. Difference in Watts from the moving average of the reference power (MMXN1.Watt) above which no smoothing shall be applied. | X | X | X | 0 | 1 | 0 |  | kW | 1 | [6 empty] | 1. |  |  | Yes
AO115 | Active Power Smoothing Upper Limit. Difference in Watts from the moving average of the reference power (MMXN.Watt) below which no smoothing shall be applied. | X | X | X | 2147483647 | 1 | 0 |  | Watts | 1 | 2 | 2 | DRCT | 1 | DRCT.DbWHi | ASG | DRCT.DRCT.DbWHi | RPS |  | Yes
AO116 | Active Power Smoothing Filter Time (Seconds). Time in seconds used to calculate the moving average of the reference load or generation (MMXN1.Watt) being smoothed. | X | X | X | 2147483647 | 1 | 0 |  | Sec | 1 | [6 empty] | 7. |  |  | Yes
AO117 | Active Power Smoothing Time Window | X | X | X | 2147483647 | 1 | 0 |  | Sec | 1 | 2 | 2 | DOPM | 7 | WinTms | ING | DOPM7.WinTms | RPS |  | Yes
AO118 | Active Power Smoothing Timeout Period | X | X | X | 2147483647 | 1 | 0 |  | Sec | 1 | 2 | 2 | DOPM | 7 | RvrtTms | ING | DOPM7.RvrtTms | RPS |  | Yes
AO119 | Active Power Smoothing Ramp Up Time | X | X | X | 2147483647 | 1 | 0 |  | Sec | 1 | 2 | 2 | DOPM | 7 | RmpTms | ING | DOPM7.RmpTms | RPS |  | Yes
AO120 | Active Power Smoothing Timeout Period | X | X | X | 2147483647 | 1 | 0 |  | Sec | 1 | 2 | 2 | DOPM | 7 | RvrtTms | ING | DOPM7.RvrtTms | RPS |  | Yes
AO121 | Active Power Smoothing Ramp Down Time | X | X | X | 2147483647 | 1 | 0 |  | Sec | 1 | 2 | 2 | DOPM | 7 | RmpTms | ING | DOPM.RmpTms | RPS |  | Yes
AO122 | Active Power Smoothing Mode Priority | X | X | X | 0 | number of modes | 1 | 0 | N/A | 1 | [6 empty] | . |  |  | Yes
AO123 | Volt-Watt Signal Meter ID | X | X | X | 2147483647 | 1 | 0 |  | N/A | 1 | [6 empty] | . |  |  | Yes
AO124 | Volt-Watt Curve Index | [7 empty] | N/A | [10 empty] | Yes
AO125 | Volt-Watt Watt Gradient | X | X | X | 2147483647 | 0.001 | 0 |  | N/A | 0.001 | [6 empty] | . |  |  | Yes
AO126 | Volt-Watt Lower Limit | X | X | X | 2147483647 | 0.001 | 0 |  | Volts | 0.001 | [6 empty] | . |  |  | Yes
AO127 | Volt-Watt Upper Limit | X | X | X | 2147483647 | 0.001 | 0 |  | Volts | 0.001 | [6 empty] | . |  |  | Yes
AO128 | Volt-Watt Filter Time (Seconds) | X | X | X | 2147483647 | 1 | 0 |  | Sec | 1 | [6 empty] | . |  |  | Yes
AO129 | Volt-Watt Time Window | X | X | X | 2147483647 | 1 | 0 |  | Sec | 1 | [6 empty] | . |  |  | Yes
AO130 | Volt-Watt Timeout Period | X | X | X | 2147483647 | 1 | 0 |  | Sec | 1 | [6 empty] | . |  |  | Yes
AO131 | Volt-Watt Ramp Up Time | X | X | X | 2147483647 | 1 | 0 |  | Sec | 1 | [6 empty] | . |  |  | Yes
AO132 | Volt-Watt Timeout Period | X | X | X | 2147483647 | 1 | 0 |  | Sec | 1 | [6 empty] | . |  |  | Yes
AO133 | Volt-Watt Ramp Down Time | X | X | X | 2147483647 | 1 | 0 |  | Sec | 1 | [6 empty] | . |  |  | Yes
AO134 | Volt-Watt Mode Priority | X | X | X | 0 | number of modes | 1 | 0 | n/a | 1 | [6 empty] | 1. |  |  | Yes
AO135 | Frequency-Watt Mode Signal Meter ID | X | X | X | 0 | 2147483647 | 1 | 0 |  | 1 | 2 | 2 |  |  |  |  | . |  |  | Yes
AO136 | Frequency-Watt Mode Curve Index | [7 empty] | N/A | [10 empty] | Yes
AO137 | Frequency-Watt Mode Target Frequency | X | X | X | 0 | 2147483647 | 0.001 | 0 | Hertz | 0.001 | 2 | 2 |  |  |  |  | . |  |  | Yes
AO138 | Frequency-Watt Mode Lower Outer Limit | X | X | X | 0 | 2147483647 | 0.001 | 0 | Hertz | 0.001 | 2 | 2 |  |  |  |  | . |  |  | Yes
AO139 | Frequency-Watt Mode Lower Inner Limit | X | X | X | 0 | 2147483647 | 0.001 | 0 | Hertz | 0.001 | 2 | 2 |  |  |  |  | . |  |  | Yes
AO140 | Frequency-Watt Mode Upper Outer Limit | X | X | X | 0 | 2147483647 | 0.001 | 0 | Hertz | 0.001 | 2 | 2 |  |  |  |  | . |  |  | Yes
AO141 | Frequency-Watt Mode Upper Inner Limit | X | X | X | 0 | 2147483647 | 0.001 | 0 | Hertz | 0.001 | 2 | 2 |  |  |  |  | . |  |  | Yes
AO142 | Frequency-Watt Mode Violation Response Delay | X | X | X | 0 | 2147483647 | 1 | 0 | MS | 1 | 2 | 2 |  |  |  |  | . |  |  | Yes
AO143 | Frequency-Watt Mode Healthy Response Delay | X | X | X | 0 | 2147483647 | 1 | 0 | MS | 1 | 2 | 2 |  |  |  |  | 1. |  |  | Yes
AO144 | Frequency-Watt Mode SoC Target | X | X | X | 0 | 1000 | 0.1 | 0 | Percent | 0.1 | 2 | 2 | DRCT | 1 | WMaxLimPct |  | DRCT.WMaxLimPct |  |  | Yes
AO145 | Frequency-Watt Mode SoC Restoration Rate | X | X | X | 0 | 2147483647 | 1 | 0 | kW | 1 | 2 | 2 |  |  |  |  | . |  |  | Yes
AO146 | Frequency-Watt Mode Time Window | X | X | X | 0 | 2147483647 | 1 | 0 | Sec | 1 | 2 | 2 |  |  |  |  | . |  |  | Yes
AO147 | Frequency-Watt Mode Timeout Period | X | X | X | 0 | 2147483647 | 1 | 0 | Sec | 1 | 2 | 2 |  |  |  |  | . |  |  | Yes
AO148 | Frequency-Watt Mode Ramp Up Time | X | X | X | 0 | 2147483647 | 1 | 0 | Sec | 1 | 2 | 2 |  |  |  |  | . |  |  | Yes
AO149 | Frequency-Watt Mode Timeout Period | X | X | X | 0 | 2147483647 | 1 | 0 | Sec | 1 | 2 | 2 |  |  |  |  | . |  |  | Yes
AO150 | Freq-Watt Emergency Ramp Down Time | X | X | X | 0 | 2147483647 | 1 | 0 | Sec | 1 | 2 | 2 |  |  |  |  | . |  |  | Yes
AO151 | Freq-Watt Emergency Mode Priority | X | X | X | 0 | number of modes | 1 | 0 | n/a | 1 | [6 empty] | 3. |  |  | Yes
AO152 | Fixed Power Factor Time Window | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DOPM | 3 | WinTms | ING | DOPM3.WinTms | INV3 |  | Yes
AO153 | Fixed Power Factor Timeout Period | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DOPM | 3 | RvrtTms | ING | DOPM3.RvrtTms | INV3 |  | Yes
AO154 | Fixed Power Factor Ramp Up Time | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DOPM | 3 | RmpTms | ING | DOPM3.RmpTms | INV3 |  | Yes
AO155 | Fixed Power Factor Ramp Down Time | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DOPM | 3 | RmpTms | ING | DOPM1.RmpTms | INV3 |  | Yes
AO156 | Fixed Power Factor Setpoint. Meaning of sign varies depending on convention and quadrant selection settings. | X | X | X | -100 | 100 | 0.01 | 0 | None | 0.01 | 2 | 2 | DRCT | 1 | OutPFSet | APC | DRCT.OutPFSet | INV3 |  | Yes | New IEC 61850 logical node
AO157 | Fixed Power Factor Reactive Power Sign <0> = Always Positive <1> = Always Negative <2> = Follows Power Factor | [15 empty] | 1. |  |  | Yes
AO158 | Fixed Power Factor Sign convention: <1> IEC – active power <2> IEEE – lead/lag | X | X | X | 1 | 3 | 1 | 0 | None | 1 | 2 | 2 | MMXU | 1 | \] | ENG | MMXU. \] | INV3 |  | Yes | New IEC 61850 name and logical node | May also be in DRCT? How do we know which MMXU?
AO159 | Fixed Power Factor Mode Priority | X | X | X | 0 | number of modes | 1 | 0 | n/a | 1 | [6 empty] | . |  |  | Yes
AO160 | Volt-VAR Control Signal Meter ID | X | X | X | 0 | 2147483647 | 1 | 0 |  | 1 | 2 | 2 | DGSM |  | WinTms |  | DGSM2.WinTms |  |  | Yes
AO161 | Volt-VAR Curve Index
AO162 | Volt-VAR Control Time Window | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DGSM | 2 | RvrtTms | ING | DGSM2.RvrtTms | INV2 |  | Yes
AO163 | Volt-VAR Control Timeout Period | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DGSM | 2 |  |  | DGSM2. |  |  | Yes
AO164 | Volt-VAR Control Ramp Up Time | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DGSM | 2 | RmpTms | ING | DGSM2.RmpTms | INV2 |  | Yes
AO165 | Volt-VAR Control Timeout Period | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DGSM | 2 |  |  | DGSM2. |  |  | Yes
AO166 | Volt-VAR Control Ramp Down Time | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DGSM | 2 | RmpTms | ING | DGSM1.RmpTms | INV2 |  | Yes
AO167 | Volt-VAR Control Deadband Lower Voltage Limit. | X | X | X | 0 | 1000 | 0.1 | 0 | Percent | 1 | 2 | 2 | RDGS | 1 | DbVMin | ASG | RDGS1.DbVMin | TV31 |  | Yes
AO168 | Volt-VAR Control Deadband Upper Voltage Limit. | X | X | X | 0 | 1000 | 0.1 | 0 | Percent | 1 | 2 | 2 | RDGS | 1 | DbVMax | ASG | RDGS.DbVMax | TV31 |  | Yes
AO169 | Volt-VAR Control Factor Mode Priority | X | X | X | 0 | number of modes | 1 | 0 | n/a | 1 | [6 empty] | #REF! |  |  | Yes
AO170 | Watt-VAr Signal Meter ID | [18 empty] | Yes
AO171 | Watt-VAr Curve Index | [18 empty] | Yes
AO172 | Watt-VAr Mode Priority | X | X | X | 0 | number of modes | 1 | 0 | n/a | 1 | [6 empty] | . |  |  | Yes
AO173 | Power Factor Correction Average PF Target | [15 empty] | . |  |  | Yes
AO174 | Power Factor Correction Lower PF Limit | X | X | X | -1 | 1 | 0.01 | 0 | N/A | 0.01 | 2 | 2 |  |  |  |  | . |  |  | Yes
AO175 | Power Factor Correction Upper PF Limit | X | X | X | 0 | 2147483647 | 1 | 0 | Sec | 1 | 2 | 2 |  |  |  |  | . |  |  | Yes
AO176 | Power Factor Correction Time Window | X | X | X | 0 | 2147483647 | 1 | 0 | Sec | 1 | 2 | 2 |  |  |  |  | . |  |  | Yes
AO177 | Power Factor Correction Timeout Period | X | X | X | 0 | 2147483647 | 1 | 0 | Sec | 1 | 2 | 2 |  |  |  |  | . |  |  | Yes
AO178 | Power Factor Correction Ramp Up Time | X | X | X | 0 | 2147483647 | 1 | 0 | Sec | 1 | 2 | 2 |  |  |  |  | . |  |  | Yes
AO179 | Power Factor Correction Timeout Period | X | X | X | 0 | 2147483647 | 1 | 0 | Sec | 1 | 2 | 2 |  |  |  |  | . |  |  | Yes
AO180 | Power Factor Correction Ramp Down Time | [15 empty] | . |  |  | Yes
AO181 | Power Factor Correction Mode Priority | X | X | X | 0 | number of modes | 1 | 0 | n/a | 1 | [6 empty] | 5.
AO182 | Pricing Mode Time window | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DOPM | 5 | WinTms | ING | DOPM5.WinTms | INV5
AO183 | Pricing Mode Timeout period | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DOPM | 5 | RvrtTms | ING | DOPM5.RvrtTms | INV5
AO184 | Pricing Mode Ramp Up Time | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DOPM | 5 | RmpTms | ING | DOPM5.RmpTms | INV5 |  |  |  | Per item 70
AO185 | Pricing Mode Ramp Down Time | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DOPM | 5 | RmpTms | ING | DOPM1.RmpTms | INV5 |  |  |  | Per item 70
AO186 | Pricing Mode Setpoint. Hundredths of local currency per Kilowatt-Hr. | X | X | X | -2147483648 | 2147483647 | 0.01 | 0 | 100ths of local currency | 0.01 | 2 | 2 | DCCT | 1 | PrcCod | ING | DCCT.PrcCod | INV5 |  |  |  | Still not well-defined
AO187 | Pricing Mode Priority | X | X | X | 0 | number of modes | 1 | 0 | n/a | 1 | [6 empty] | #REF!
AO188 | Curve Edit Selector Writing to this point selects which of the curves can currently be viewed and changed. | X | X | X | 1 | 2147483647 | 1 | 0 | n/a | 1 | 2 | 2 | DGSM FMAR | n | Not mapped. Selects which instance of DGSM and FMAR greater than 10 are "visible". |  | #REF! |  |  | Yes | new
AO189 | Curve Mode Type <0> Curve disabled <1> Not applicable / Unknown <2> Volt-Var modes VV11-VV12 <3> Frequency-Watt mode FW22 <4> Watt-VAr mode WP42 <5> Voltage-Watt modes VW51-VW52 <6> Remain Connected <7> Temperature mode <8> Pricing signal mode High Voltage ride-through curves <9> HVRT Must Trip <10> HVRT Momentary Cessation <11> HVRT Continuous Operation Low Voltage ride-through curves <12> LVRT Must Trip <13> LVRT Momentary Cessation <14> LVRT Continuous Operation High Frequency ride-through curves <15> HFRT Must Trip <16> HFRT Mandatory Operation <17> HFRT Continuous Operation Low Frequency ride-through curves <18> LFRT Must Trip <19> LFRT Mandatory Operation <20> LFRT Continuous Operation | X | X | X | 0 | 8 | 1 | 0 | n/a | 1 | 2 | 2 | DGSM | n | ModTyp | ENG | DGSMn.ModTyp | CRV |  | Yes | new
AO190 | Curve Time Window | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DGSM | n | WinTms | ING | DGSMn.WinTms | CRV |  | Yes | new
AO191 | Curve Ramp Time | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DGSM | n | RmpTms | ING | DGSMn.RmpTms | CRV |  | Yes | new
AO192 | Curve Revert Time | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | DGSM | n | RvrtTms | ING | DGSMn.RvrtTms | CRV |  | Yes | new
AO193 | Curve Number of Points | X | X | X | 0 | 100 | 1 | 0 | n/a | 1 | 2 | 2 | FMAR | n | PairArray. NumPts | CSG | FMARn.PairArray. NumPts | CRV |  | Yes | new
AO194 | Curve Maximum Number of Points | X | X | X | 0 | 100 | 1 | 0 | n/a | 1 | 2 | 2 | FMAR | n | PairArray. MaxPts | CSG | FMARn.PairArray. MaxPts | CRV |  | Yes | new
AO195 | Independent (X-Value) Units for Curve <0> Curve disabled <1> Not applicable / Unknown <4> Time <29> Voltage <33> Frequency <38> Watts <23> Celsius Temperature <100> Price in hundredths of local currency <129> Percent Voltage <133> Percent Frequency <138> Percent Watts <233> Frequency Deviation | X | X | X | 0 | 233 | 1 | 0 | n/a | 1 | 2 | 2 | FMAR | n | IndpUnits | ENG | FMARn.IndpUnits | CRV |  | Yes | new
AO196 | Dependent (Y-Value) Units for Curve <0> Curve disabled <1> Not applicable / unknown <2> VArs as percent of max VArs (VARMax) <3> VArs as percent of max available VArs (VArAval) <4> Vars as percent of max Watts (Wmax) – not used <5> Watts as percent of max Watts (Wmax) <6> Watts as percent of frozen active power (DeptSnptRef) <7> Power Factor in EEI notation <8> Volts as a percent of the nominal voltage (VRef) <99+> Other | X | X | X | 0 | 255 | 1 | 0 | n/a | 1 | 2 | 2 | FMAR | n | DeptRef | ENG | FMARn.DeptRef | CRV |  | Yes | new
AO197 | Curve Time Constant. Time constant of the low-pass filter to be applied to the output of the Curve, in seconds. This is the 3T (tau) value specifying the time at which a step change of the Dependent Variable (e.g. Watts) will settle to 95% of the final value. | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | FMAR | n | RmpPT1Tms | ENG | FMARn.RmpPT1Tms | CRV |  | Yes | new | Optional. Should we include?
AO198 | Curve Decreasing Max Ramp Rate. The maximum rate at which the dependent value (output, Y-Value) may be reduced in response to changes in the independent value (input, X-Value). This is represented in terms of % of Reference value (e.g. WMax) per minute . | X | X | X | 0 | 1000 | 0.1 | 0 | Percent per min |  | 2 | 2 | FMAR | n | RmpDecDmm | ENG | FMARn.RmpDecDmm | CRV |  | Yes | new | Optional. Should we include?
AO199 | Curve Increasing Max Ramp Rate. The maximum rate at which the dependent value (output, Y-Value) may be reduced in response to changes in the independent value (input, X-Value). This restriction is applied after the low-pass filter. This value is represented in terms of % of Reference value (e.g. WMax) per minute . | X | X | X | 0 | 1000 | 0.1 | 0 | Percent per min | 1 | 2 | 2 | FMAR | n | RmpIncTmm | ENG | FMARn.RmpIncTmm | CRV |  | Yes | new | Optional. Should we include?
AO200 | Curve Release Max Ramp Rate. The maximum rate at which the dependent value (ouput, Y-Value) may be increased after releasing the frozen value of snap shot function. This restriction is applied after the low-pass filter. This value is represented in terms of % of Reference value (e.g. WMax) per minute. | X | X | X | 0 | 1000 | 0.1 | 0 | Percent per min | 1 | 2 | 2 | FMAR | n | RmpRsUp | ENG | FMARn.RmpRsUp | CRV |  | Yes | new | Optional. Should we include?
AO201 | Curve Dependent Variable Snapshot Reference. This is the snapshot value of the dependent variable (Y-Value, e.g. Watts) stored when the independent variable (X-Value, e.g. Frequency) reaches a threshold value. Currently only used with Curve Mode Type <223> Frequency Deviation. | X | X | X | Varies depending on Curve Mode Type |  |  | 0 | Varies | Varies | 2 | 2 | FMAR | n | DeptSnptRef |  | FMARn.DeptSnptRef |  |  | Yes
AO202 | Curve Dependent Variable Snapshot Start. Deviation from nominal value of the independent variable (X-Value, e.g. Frequency) at which to take a snapshot of the dependent variable (e.g. WRef) and start constraining the output ( e.g. Watts). Currently only used with Independent Value Units of <223> Frequency Deviation. | X | X | X | see table depending on Mode Type |  |  | 0 | Varies | (1%) | 2 | 2 | FMAR | n | DeptRefStr | ENG | FMARn.DeptRefStr | FW22 |  | Yes | new | Optional. Should we include?
AO203 | Curve Dependent Variable Snapshot Stop. Deviation from nominal value of the independent variable (X-Value, e.g. Frequency) at which to release the output (Y-Value, e.g. Watts). Currently only used with Independent Curve Units of <223> Frequency Deviation. | X | X | X | see table depending on Mode Type |  |  | 0 | Varies | (1%) | 2 | 2 | FMAR | n | DeptRefStop | ENG | #REF! | FW22 |  | Yes | new | Optional. Should we include?
AO204 | Curve Point 1 X-Value | X | X | X | see scaling table depending on Mode Type |  |  | 0 | Varies | 1 | 2 | 2 | FMAR | n | PairArray.CrvPts[0].xVal | CSG | FMARn.PairArray.CrvPts[0].xVal | CRV |  | Yes | new
AO205 | Curve Point 1 Y-Value | X | X | X | see scaling table depending on Mode Type |  |  | 0 | Varies | 1 | 2 | 2 | FMAR | n | PairArray.CrvPts[0].yVal | CSG | FMARn.PairArray.CrvPts[0].yVal | CRV |  | Yes | new
AO206 | Curve Point 2 X-Value | X | X | X | see scaling table depending on Mode Type |  |  | 0 | Varies | 1 | 2 | 2 | FMAR | n | PairArray.CrvPts[1].xVal | CSG | FMARn.PairArray.CrvPts[1].xVal | CRV |  | Yes | new
AO207 | Curve Point 2 Y-Value | X | X | X | see scaling table depending on Mode Type |  |  | 0 | Varies | 1 | 2 | 2 | FMAR | n | PairArray.CrvPts[1].yVal | CSG | FMAR.PairArray.CrvPts[1].yVal | CRV |  | Yes | new
AO208 - AO396 | Curve X-Value, Y-Value pairs for curve points 3 -99 | [18 empty] | Yes
AO397 | Curve Point 100 X-Value | X | X | X | see scaling table depending on Mode Type |  |  | 0 | Varies | 1 | 2 | 2 | FMAR | n | PairArray.CrvPts[100].xVal | CSG | FMARn.PairArray.CrvPts[100].xVal | CRV |  | Yes | new
AO398 | Curve Point 100 Y-Value | X | X | X | see scaling table depending on Mode Type |  |  | 0 | Varies | 1 | 2 | 2 | FMAR | n | PairArray.CrvPts[100].yVal | CSG | FMARn.PairArray.CrvPts[100].yVal | CRV |  | Yes | new
S (S = 407 for this version of the specification) | Schedule to Edit Selector. Selects which of the schedules can be currently viewed and changed. | X | X | X | 0 | 2147483647 | 1 | 0 | n/a | 1 | 2 | 2 | FSCC | 1 | Not mapped. Selects which instance of FSCH is currently visible. |  | FSCCn.Not mapped. Selects which instance of FSCH is currently visible. | SCD |  | Yes | new
#REF! | Selected Schedule Identity | X | X | X | 0 | 2147483647 | 1 | 0 | n/a | 1 | 2 | 2 | FSCH | n | SchdId | ING | FSCHn.SchdId | SCD |  | Yes
S+1 | Selected Schedule Priority (0 invalid, higher supersedes lower) | X | X | X | 0 | 2147483647 | 1 | 0 | n/a | 1 | 2 | 2 | FSCH | n | SchdPrio | ENG | FSCH1.SchdPrio | SCD |  | Yes | new
#REF! | Selected Schedule Type (yVal) <0> Not applicable / Unknown <1> Active power (2.3.4), Percent of maximum <2> Reserved <3> Power factor ( 2.3.5) <4> Reserved <5> Price for active power (2.3.7) <6> Price for reactive power <7> Reserved <8> Curve Identifier (2.3.6) (previously Volt/VAR Array) <9> Charge/Discharge rate (2.3.6), percent of maximum <10> State of Charge (percent of full charge) <11> Power factor correction (on/off) <12> Peak Power Limiting (on/off) <13> Load or Generation following (on/off) | X | X | X | 0 | 3 | 1 | 0 | N/A | 1 | 2 | 2 | FSCH | 1 | SchdVal.valEq | SCR | FSCH.SchdVal.valEq | SCD |  | Yes | New IEC 61850 name and logical node. Combined MESA and existing DNP3 forming superset of types. | Changed name to "Selected Schedule Type" per item #80.
#REF! | Selected Schedule Start Time Long 1. Upper 32 bits of 64-bit Date/time expressed as the number of seconds January 1st, 1970. | X | X | X | 0 | 2147483647 | 1 | 0 | Sec | 1 | 2 | 2 |  |  |  |  | . |  |  | Yes
S+2 | Selected Schedule Start Time Long 2. Lower 32 bits of 64-bit Date/time expressed as the number of seconds from January 1st, 1970. | X | X | X | 0 | 2147483647 | 1 | 0 | Sec | 1 | 2 | 2 |  |  |  |  | . |  |  | Yes
S+3 | Selected Schedule Repeat Interval Interval between actions after the initial occurrence. A zero value means the schedule is not repeated. | X | X | X | 0 | 2147483647 | 1 | 0 | N/A | 1 | 2 | 2 |  |  |  |  | . |  |  | Yes
S+4 | Selected Schedule Repeat Interval Units <0> = No Repeat <1> = Seconds <2> = Minutes <3> = Hours <4> = Days <5> = Weeks <6> = Months <7> = Months on Same Day of Week <8> = Months on Same Day of Week from End | X | X | X | 0 | 8 | 1 | 0 | N/A | 1 | 2 | 2 |  |  |  |  | n. |  |  | Yes
S+5 | Selected Schedule Number of Points | X | X | X | 0 | 100 | 1 | 0 | n/a | 1 | 2 | 2 | FSCH | n | SchdVal.numPts | SCR | FSCHn.SchdVal.numPts | SCD |  | Yes | new
S+6 | Selected Schedule Point [1] Time Offset Number of seconds from the start of the schedule when this point becomes active. | X | X | X | 0 | 2147483647 | 1 | 0 | varies | 1 | 2 | 2 | FSCH | n | SchdVal.val[ 0 ] | SCR | FSCH.SchdVal.val[ 0 ] | SCD |  | Yes | new
S+7 | Selected Schedule Point[1] Value | X | X | X | -2147483648 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 |  |  |  |  | n. |  |  | Yes
S+8 | Selected Schedule Point [2] Time Offset | X | X | X | 0 | 2147483647 | 1 | 0 | varies | 1 | 2 | 2 | FSCH | n | SchdVal.val[ 1 ] | SCR | FSCH.SchdVal.val[ 1 ] | SCD |  | Yes | new
S+9 | Selected Schedule Point[2] Value | X | X | X | -2147483648 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 |  |  |  |  | . |  |  | Yes
S10 - S197 | Selected Schedule Time Offset and Value points 3 - 99. | [19 empty] | new
S+198 | Selected Schedule Point [100] Time Offset | X | X | X | 0 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 | FSCH | n | SchdVal.tmOffset[100] | SCR | FSCH.SchdVal.tmOffset[100] | SCD |  | Yes | new
S+199 | Selected Schedule Point[100] Value | X | X | X | -2147483648 | 2147483647 | 1 | 0 | Seconds | 1 | 2 | 2 |  |  |  |  | n. |  |  | Yes
HM | Meter #1 Active power at connection point – high threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Watts | (1%) | 2 | 2 | MMXU |  | TotW | MV | MMXU.TotW |  |  | Yes
#REF! | Meter #1 Active power at connection point – low threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Watts | (1%) | 2 | 2 | MMXU |  | TotW | MV | MMXU.TotW |  |  | Yes
HM+1 | Meter #1 Reactive power at connection point – high threshold | X | X | X | 0 | 2147483647 | 1 | 0 | VARs | (1%) | 2 | 2 | MMXU |  | TotVAr | MV | MMXU.TotVAr |  |  | Yes
#REF! | Meter #1 at Reactive power at connection point – low threshold | X | X | X | 0 | 2147483647 | 1 | 0 | VARs | (1%) | 2 | 2 | MMXU |  | TotVAr | MV | MMXU.TotVAr |  |  | Yes
#REF! | Meter #1 at Power factor at connection point – high threshold | X | X | X | -100 | 100 | 0.01 | 0 | None | 0.01 | 2 | 2 | MMXU |  | TotPF | MV | MMXU.TotPF |  |  | Yes
HM+2 | Meter #1 at Power factor at connection point – low threshold | X | X | X | -100 | 100 | 0.01 | 0 | None | 0.01 | 2 | 2 | MMXU |  | TotPF | MV | MMXU.TotPF |  |  | Yes
HM+3 | Meter #1 Phase A Volts – high threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Volts | (1%) | 2 | 2 | MMXU |  | PhV | WYE | MMXU.PhV |  |  | Yes |  | What does threshold mean?
HM+4 | Meter #1 Phase A Volts – low threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Volts | (1%) | 2 | 2 | MMXU |  | PhV | WYE | MMXU.PhV |  |  | Yes
HM+5 | Meter #1 Phase B Volts – high threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Volts | (1%) | 2 | 2 | MMXU |  | PhV | WYE | MMXU.PhV |  |  | Yes
HM+6 | Meter #1 at Phase B Volts – low threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Volts | (1%) | 2 | 2 | MMXU |  | PhV | WYE | MMXU.PhV |  |  | Yes
HM+7 | Meter #1 at Phase C Volts – high threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Volts | (1%) | 2 | 2 | MMXU |  | PhV | WYE | MMXU.PhV |  |  | Yes
HM+8 | Meter #1 at Phase C Volts – low threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Volts | (1%) | 2 | 2 | MMXU |  | PhV | WYE | MMXU.PhV |  |  | Yes
. . . | Meter #2. . . . Meter #m-1 points | [18 empty] | Yes
HM+ mhao(m-1) | Meter #m Active power at connection point – high threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Watts | (1%) | 2 | 2 | MMXU |  | TotW | MV | MMXU.TotW |  |  | Yes
#REF! | Meter #m Active power at connection point – low threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Watts | (1%) | 2 | 2 | MMXU |  | TotW | MV | MMXU.TotW |  |  | Yes
HM+ mhao(m-1)+1 | Meter #m Reactive power at connection point – high threshold | X | X | X | 0 | 2147483647 | 1 | 0 | VARs | (1%) | 2 | 2 | MMXU |  | TotVAr | MV | MMXU.TotVAr |  |  | Yes
#REF! | Meter #m Reactive power at connection point – low threshold | X | X | X | 0 | 2147483647 | 1 | 0 | VARs | (1%) | 2 | 2 | MMXU |  | TotVAr | MV | MMXU.TotVAr |  |  | Yes
#REF! | Meter #m Power factor at connection point – high threshold | X | X | X | -100 | 100 | 0.01 | 0 | None | 0.01 | 2 | 2 | MMXU |  | TotPF | MV | MMXU.TotPF |  |  | Yes
HM+ mhao(m-1)+2 | Meter #m Power factor at connection point – low threshold | X | X | X | -100 | 100 | 0.01 | 0 | None | 0.01 | 2 | 2 | MMXU |  | TotPF | MV | MMXU.TotPF |  |  | Yes
HM+ mhao(m-1)+3 | Meter #m Phase A Volts – high threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Volts | (1%) | 2 | 2 | MMXU |  | PhV | WYE | MMXU.PhV |  |  | Yes
HM+ mhao(m-1)+4 | Meter #m Phase A Volts – low threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Volts | (1%) | 2 | 2 | MMXU |  | PhV | WYE | MMXU.PhV |  |  | Yes
HM+ mhao(m-1)+5 | Meter #m Phase B Volts – high threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Volts | (1%) | 2 | 2 | MMXU |  | PhV | WYE | MMXU.PhV |  |  | Yes
HM+ mhao(m-1)+6 | Meter #m Phase B Volts – low threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Volts | (1%) | 2 | 2 | MMXU |  | PhV | WYE | MMXU.PhV |  |  | Yes
HM+ mhao(m-1)+7 | Meter #m Phase C Volts – high threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Volts | (1%) | 2 | 2 | MMXU |  | PhV | WYE | MMXU.PhV |  |  | Yes
HM+ mhao(m-1)+8 | Meter #m Phase C Volts – low threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Volts | (1%) | 2 | 2 | MMXU |  | PhV | WYE | #REF! |  |  | Yes
HI | Inverter #1 active power output – high threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Watts | (1%) | 2 | 2 | MMXU |  | TotW | MV | MMXU.TotW |  |  | Yes | Fixed missing point index
#REF! | Inverter #1 active power output – low threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Watts | (1%) | 2 | 2 | MMXU |  | TotW | MV | MMXU.TotW |  |  | Yes
HI+1 | Inverter #1 reactive output – high threshold | X | X | X | 0 | 2147483647 | 1 | 0 | VARs | (1%) | 2 | 2 | MMXU |  | TotVAr | MV | MMXU.TotVAr |  |  | Yes
#REF! | Inverter #1 reactive output – low threshold | X | X | X | 0 | 2147483647 | 1 | 0 | VARs | (1%) | 2 | 2 | MMXU |  | TotVAr | MV | MMXU.TotVAr |  |  | Yes
#REF! | Inverter #1 Current output frequency – high threshold | X | X | X | 0 | 70000 | 0.001 | 0 | Hz | 1 | 2 | 2 | MMXU |  | Hz | MV | MMXU.Hz |  |  | Yes
HI+2 | Inverter #1 Current output frequency – low threshold | X | X | X | 0 | 70000 | 0.001 | 0 | Hz | 1 | 2 | 2 | MMXU |  | Hz | MV | MMXU.Hz |  |  | Yes
HI+3 | Inverter #1 DC Inverter input power – high threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Watts | (1%) | 2 | 2 | MMDC |  | Watt | MV | MMDC.Watt |  |  | Yes
HI+4 | Inverter #1 DC Inverter input power – low threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Watts | (1%) | 2 | 2 | MMDC |  | Watt | MV | MMDC.Watt |  |  | Yes
HI+5 | Inverter #1 DC input current available – high threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Amps | (1%) | 2 | 2 | MMDC |  | Amp | MV | MMDC.Amp |  |  | Yes
HI+6 | Inverter #1 DC input current available – low threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Amps | (1%) | 2 | 2 | MMDC |  | Amp | MV | MMDC.Amp |  |  | Yes
HI+7 | Inverter #1 DC voltage between DER system and inverter – high threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Volts | (1%) | 2 | 2 | MMDC |  | Vol | MV | MMDC.Vol |  |  | Yes |  | Changed per item #36
HI+8 | Inverter #1 DC voltage between DER system and inverter – low threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Volts | (1%) | 2 | 2 | MMDC |  | Vol | MV | MMDC.Vol |  |  | Yes |  | Changed per item #36
. . . | Inverter #2 through Inverter #p-1 points | [18 empty] | Yes
HI+ ihao(p-1) | Inverter #p active power output – high threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Watts | (1%) | 2 | 2 | MMXU |  | TotW | MV | MMXU.TotW |  |  | Yes
#REF! | Inverter #p active power output – low threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Watts | (1%) | 2 | 2 | MMXU |  | TotW | MV | MMXU.TotW |  |  | Yes
HI+ ihao(p-1) +1 | Inverter #p reactive output – high threshold | X | X | X | 0 | 2147483647 | 1 | 0 | VARs | (1%) | 2 | 2 | MMXU |  | TotVAr | MV | MMXU.TotVAr |  |  | Yes
#REF! | Inverter #p reactive output – low threshold | X | X | X | 0 | 2147483647 | 1 | 0 | VARs | (1%) | 2 | 2 | MMXU |  | TotVAr | MV | MMXU.TotVAr |  |  | Yes
#REF! | Inverter #p Current output frequency – high threshold | X | X | X | 0 | 70000 | 0.001 | 0 | Hz | 0.001 | 2 | 2 | MMXU |  | Hz | MV | MMXU.Hz |  |  | Yes
HI+ ihao(p-1) +2 | Inverter #p Current output frequency – low threshold | X | X | X | 0 | 70000 | 0.001 | 0 | Hz | 0.001 | 2 | 2 | MMXU |  | Hz | MV | MMXU.Hz |  |  | Yes
HI+ ihao(p-1) +3 | Inverter #p DC Inverter input power – high threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Watts | (1%) | 2 | 2 | MMDC |  | Watt | MV | MMDC.Watt |  |  | Yes
HI+ ihao(p-1) +4 | Inverter #p DC Inverter input power – low threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Watts | (1%) | 2 | 2 | MMDC |  | Watt | MV | MMDC.Watt |  |  | Yes
HI+ ihao(p-1) +5 | Inverter #p DC input current available – high threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Amps | (1%) | 2 | 2 | MMDC |  | Amp | MV | MMDC.Amp |  |  | Yes
HI+ ihao(p-1) +6 | Inverter #p DC input current available – low threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Amps | (1%) | 2 | 2 | MMDC |  | Amp | MV | MMDC.Amp |  |  | Yes
HI+ ihao(p-1) +7 | Inverter #p DC voltage between DER system and inverter – high threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Volts | (1%) | 2 | 2 | MMDC |  | Vol | MV | MMDC.Vol |  |  | Yes |  | Changed per item #36
HI+ ihao(p-1) +8 | Inverter #p DC voltage between DER system and inverter – low threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Volts | (1%) | 2 | 2 | MMDC |  | Vol | MV | #REF! |  |  | Yes |  | Changed per item #36
HB | Battery #1 External voltage - high threshold. Voltage between battery charger and battery. | X | X | X | 0 | 2147483647 | 1 | 0 | Volts | (1%) | 2 | 2 | ZBAT |  | Vol | MV | ZBAT.Vol |  |  | Yes
#REF! | Battery #1 External voltage - low threshold. Voltage battery charger and battery. | X | X | X | 0 | 2147483647 | 1 | 0 | Volts | (1%) | 2 | 2 | ZBAT |  | Vol | MV | ZBAT.Vol |  |  | Yes
HB+1 | Battery #1 Internal voltage – high threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Volts | (1%) | 2 | 2 | ZBAT |  | InBatV | MV | ZBAT.InBatV |  |  | Yes
#REF! | Battery #1 Internal voltage – low threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Volts | (1%) | 2 | 2 | ZBAT |  | InBatV | MV | ZBAT.InBatV |  |  | Yes
. . . | Battery #2 . . . Battery #b-1 points | [18 empty] | Yes
HB+ bhao(b-1) ) | Battery #b External voltage - high threshold. Voltage between battery charger and battery. | X | X | X | 0 | 2147483647 | 1 | 0 | Volts | (1%) | 2 | 2 | ZBAT |  | Vol | MV | ZBAT.Vol |  |  | Yes
#REF! | Battery #b External voltage - low threshold. Voltage between battery charger and battery. | X | X | X | 0 | 2147483647 | 1 | 0 | Volts | (1%) | 2 | 2 | ZBAT |  | Vol | MV | ZBAT.Vol |  |  | Yes
HB+ bhao(b-1) )+1 | Battery #b Internal voltage – high threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Volts | (1%) | 2 | 2 | ZBAT |  | InBatV | MV | ZBAT.InBatV |  |  | Yes
#REF! | Battery #b Internal voltage – low threshold | X | X | X | 0 | 2147483647 | 1 | 0 | Volts | (1%) | 2 | 2 | ZBAT |  | InBatV | MV | #REF! |  |  | Yes